Department of Labor and

Workforce Development

ADMINISTRATIVE SERVICES

Management Services

PO Box 111149

Juneau, Alaska 99811

Main: 907.465.5980

Fax: 907-465-2107

Invitation for Quotes #721AVC1160

AVTEC Welding Ventilation

Additional Information

Construction Period – The Applied Technology facility houses students in multiple areas during the school year.  The area where the work in this project is, Room 122, will be occupied by students until May 18, 2021.  From this point until approximately August 15, 2021 the area will be vacant and available for construction.  Before May 18, there will only be limited access to this room and no construction activities may occur.

Housing – There is some limited available housing on the AVTEC campus that may be utilized by construction personnel while working directly on this project.  This housing has furniture, but occupants will need to provide their own bedding, cookware, dishes and utensils.

Food – The AVTEC campus has a cafeteria available for students and staff.  This service may also be available for contractor use depending on the status of the Pandemic, until May 19, 2021, at which time it will close down for the summer break.  While open and provided the Pandemic has abated, the cafeteria may be available for meals for construction personnel working directly on this project.  Contractor should plan for alternative food services.

Questions and Answers – This solicitation is a rebid of a previous Invitation for Quotes.  Below are the questions received and answers provided during that process from prospective vendors.

- Would you like the contractors to include electrical engineering and subcontractor work in our bid?

Response – Contractors should include all costs associated with completing the Scope of Work in their bid.

- For the Makeup Air Unit (MAU) – is there Natural Gas on site?

Response – There is no Natural Gas on site.

- If hydronic, is there enough boiler capacity for the new equipment?

Response – Yes

- Is Galvanized Steel ok to use for the hood and duct work?

Response – Yes

- What kind of power requirements do you have on site?

Response – There is availability of 120 volt, 3 phase power for the exhaust fan.

- The ventilation scheme indicated in the statement of work and supporting documents eliminates the source capture exhaust, and only provides general booth exhaust from above.  This doesn’t allow welding fumes to be captured without passing through the users breathing zone and I have concerns about the health of the user in this configuration.

Response – The end user was provided various options for this item and selected this one as the most appropriate for their usage.

- The amount of exhaust indicated in the statement of work is approximately 12,200 cfm (welding & grinding) with 11,000 cfm being continuous.  They propose adding a heat recovery AHU (6,000 cfm) & heat recovery coil.  It looks like the existing AHU would need to remain to provide additional make up air.  While I haven’t analyzed the entire building heating system, I am doubtful that the existing heating system has capacity to heat the space and temper make-up air, which would increase potential for freezing hydronic coils and sprinkler piping.

Response – Actual practice will make the provided design sufficient to meet program needs.

- The statement of work indicates the dust collector could be located inside or outside the building as space allows.  I think the dust collector and associated fans would need to be located outside due to limited interior space. This appears to place the desired heat recovery coil located in the exhaust airstream outside the building, which may be possible, however it might not be as effective during the colder months.

Response – The Statement of Work allows for the placement of the dust collector outside if necessary.  If placed outside, the exhaust air duct must be insulated to the point of termination and also the heat recovery coil would require insulation for maximum effectiveness.

- Are betterments going to be entertained? If so, we have one, but would expect the betterment to be kept private.

Response – This Invitation for Quotes is set to award to the lowest priced quote based on the Scope of Work as provided without consideration of any alternate proposals.

- Can you please provide existing Arch/Structural/Electrical drawings for this project?

Response – Please see attached documents related to the original construction of this facility.

- Is the boiler big enough?

Response – This building is supplied by three (3) Weil-McLain P-WGO-6 Oil-Fired Boilers

- What is the boilers actual capacity?

Response – See response above.

- Where is the boiler room?

Response – The boilers are located above the Ex. Welding Shop as shown on the drawings.

- The attached MAU, along with the basis of design dust collector are added electrical loads for the project. Does the existing electrical service have capacity?

Response - Yes

- Do the panels have capacity?

Response - Yes

- Where are the panels located (see question #2)?

Response – The electrical panels are located in both the Pipe Welding Shop and the Grinding Room.

- Does the building have 3 phase power? The Q&A response to this question was unclear.

Response - Yes

- Are there any environment requirements for new equipment? I.E. salt spray to provide an approximant 20-year life span.

Response - No

- Do we have to place the MAU outside where is the preferred location?  Alternative locations are the roof (structural concerns) or in the room (spatial concerns).

Response – The current MAU is located inside the building.  The successful contractor may propose alternate locations as part of their design for review by the owner.

Brad Waldron

Procurement Officer