## Final FY24 ISR_InspectedAssetUs
Priority | QUALITY RATING | QUAL SCORE | UM | UM AMT | Org | ORG_NAME | SITE_UID | SITE_CODE | SITE_NAME | SITE_CITY | ASSET_UID | FACNO | FACILITY_CLASS | CATEGORY_GROUP | BASIC_CATEGORY | FAC | CATCODE | CATCODE_DESC | AGE | FACILITY_BUILT_DATE | MISSION_RATING | MISSION_SCORE | MODERNIZATION_COST | RESTORATION_COST | Stat_RM | RM_Score | RMCOST | ASSETUSE_ERV | BLDRDATE | RATINGDATE | RATEDFY | NEXTRATINGFY | RATING_GROUP | COMMENTS_GENERAL | COMMENTS_QIC_OVERWRITE | INSPECTOR_FIRSTNAME | INSPECTOR_LASTNAME | INSPECTION_DATE | QUALIFIER_CODE | QUALIFIER_DESCRIPTION
0 | 1 | 97.74 | SF | 17044 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1444602 | 49139 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 2 | 2022-04-14 | 2 | 88.6 | 2608732.3 | 517320.74 | 2 | 86.51 | 3085927.02 | 22883616.71 |  | 2024-01-24 19:10 | 2024 | 2029 | 2 | Elevator is inoperable and outside warranty; contracting repair and also for inscpection/certification. |  | Jeffrey | Herrick | 2023-10-16 06:00
0 | 1 | 93.59 | SF | 21799 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1444602 | 49139 | Supply | Covered Storage | Installation and Organization | Storage and Customer Issue | 44227 | Central Issue F | 2 | 2022-04-14 | 2 | 85.66 | 1103305.76 | 492981.09 | 3 | 79.96 | 1541871.53 | 7693903.51 |  | 2023-07-20 14:00 | 2023 | 2028 | 2 | No sustainable design nor smart network tied to the installation.Needs a lobby/arctic entry.Lacks showers/lockers. |  | Jeffrey | Herrick | 2023-07-17 06:00
0 | 1 | 91.48 | SF | 6000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1444603 | 49138 | Supply | Covered Storage | Installation and Organization | Covered Storage Shed, Installa | 44262 | Veh Str Shed In | 2 | 2022-04-14 | 3 | 73.33 | 810609.55 | 258931.75 | 3 | 66.86 | 1007129.88 | 3039405.87 |  | 2023-07-20 14:14 | 2023 | 2028 | 2 | No sustainable design features.Facility is uninsulated and unheated except for mech room.No loading dock nor ramp.Very constrained truck area due to unnecessary security fence.No latrines nor plumbing.Lightning arresting system damaged by heavy snow/ice from sloped roof. |  | Jeffrey | Herrick | 2023-07-20 06:00
0 | 1 | 90.69 | SF | 4036 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1416682 | 47422 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 5 | 2018-11-16 | 3 | 68.75 | 1143181.52 | 340645.16 | 3 | 61.5 | 1408265.28 | 3658180.85 |  | 2024-08-19 14:34 | 2024 | 2029 | 2 | Overhead cover for aircraft parts and containers. No lighting |  | Jeffrey | Herrick | 2024-07-31 06:00
0 | 2 | 88.41 | SF | 438 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 995577 | 49010 | Housing & Community | Outdoor Morale, Welfare, and R | Outdoor Entertainment Faciliti | Pavilion | 75052 | Rec Shelter | 15 | 2009-03-16 | 3 | 69.05 | 50592.18 | 18952.2 | 3 | 60.01 | 65374.55 | 163464.23 |  | 2024-08-22 15:55 | 2024 | 2029 | 2 | Outdoor pavilion; no power, lighting nor utilities |  | Jeffrey | Herrick | 2024-08-01 06:00
0 | 2 | 86.71 | SF | 5719 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190977 | 57428 | Maintenance & Production | Maintenance Facilities | Installation Repair and Operat | Facility Engineer Maintenance | 21910 | Eng/Housing Mnt | 73 | 1951-05-25 | 3 | 63.45 | 2490618.25 | 905498.61 | 4 | 52.51 | 3236303.13 | 6814277.01 |  | 2021-06-30 16:47 | 2021 | 2026 | 2 | Poor lighting and drainage.Not handicap accessible.No lobby.No Loading dock or ramp.Limited MHE capability.No standby power generator, no UPS.Small radius truck area.Stairs need anti-skid.No security measures. |  | Jeffrey | Herrick | 2021-06-30 06:00
0 | 2 | 85.75 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1484148 | 57406 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 7 | 2017-01-02 | 4 | 55.56 | 1608746.98 | 515878.33 | 4 | 45.61 | 1968800.14 | 3620042.71 |  | 2022-08-24 13:37 | 2022 | 2027 | 2 | Pre-Engineered building; poor insulation, poor drainage and lighting. No plumbing nor latrines.HVAC is inefficient unit heaters.No security systems.No fire panel nor suppression systems.No loading dock nor ramp; very limited MHE capability. |  | Jeffrey | Herrick | 2022-08-23 06:00 | 25 | Incomplete Rating
0 | 2 | 84.4 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1340061 | 49196 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 7 | 2017-01-02 | 4 | 54.1 | 1672539.18 | 568530.24 | 4 | 44.41 | 2025523.47 | 3643876.2 |  | 2024-04-18 19:12 | 2024 | 2029 | 2 | Has no controlled humidity unit; 4 unit heaters only.No loading dock, ramp, dunnage storagePoor drainage and lighting exterior.No security measure or fire suppression.No loading dock or ramp.No water or sewer.No NIPR or LAN or phones. |  | Jeffrey | Herrick | 2024-04-18 06:00
0 | 2 | 83.99 | SF | 800 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 606425 | 49000 | Operation & Training | Training Facilities | Training Buildings | Applied Instruction Building | 17136 | Auto-Aid Inst | 33 | 1991-06-17 | 3 | 72.22 | 290583.3 | 167433.51 | 4 | 58.65 | 432480.86 | 1046016.19 |  | 2024-08-19 14:52 | 2024 | 2029 | 2 |  |  | Jeffrey | Herrick | 2024-07-01 06:00
0 | 2 | 83.78 | SF | 1501 | 020NG | Alaska National Guard | 1821 | FXSB0001 | ELMENDORF AFB SITE 1 | ELMENDORF AIR FORCE BASE | 423648 | 9311 | Operation & Training | Land Operational Facilities | Airfield Operational Buildings | Aviation Operations Building | 14110 | Afld Ops Bldg | 26 | 1998-01-01 | 3 | 60.87 | 802574.62 | 332663.95 | 4 | 48.93 | 1047438.62 | 2051046.82 |  | 2020-05-27 21:05 | 2020 | 2025 | 2 |  |  | Jeffrey | Herrick | 2020-05-20 06:00 | 25 | Incomplete Rating
0 | 2 | 83.57 | SF | 4500 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295788 | 57423 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 36 | 1988-01-01 | 4 | 40 | 2443528.83 | 669077.1 | 4 | 29.71 | 2862431.15 | 4072548.05 |  | 2021-06-30 17:35 | 2021 | 2026 | 2 | Facility is a 3-sided pole barn |  | Jeffrey | Herrick | 2021-06-30 06:00 | 25 | Incomplete Rating
0 | 2 | 83.55 | SF | 2634 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295804 | 57425 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 25 | 1999-01-01 | 4 | 57.67 | 1015705.17 | 394622.91 | 4 | 47.08 | 1269699.05 | 2399492.48 |  | 2021-06-30 17:29 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.No latrines.No standby power generator. |  | Jeffrey | Herrick | 2021-06-30 06:00 | 25 | Incomplete Rating
0 | 2 | 83.02 | SF | 960 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1340063 | 57402 | Operation & Training | Land Operational Facilities | Ground Operational Buildings | Emergency Operations Center / | 14162 | Scif | 9 | 2014-12-01 | 4 | 49.19 | 836394.2 | 279491.85 | 4 | 37.95 | 1021345.4 | 1646121.24 |  | 2024-07-18 19:11 | 2024 | 2029 | 2 | A semi secure vault; does not meet all SCIF criteria. Not complete nor usable as constructed. Needs major modernization or re-categorized. |  | Jeffrey | Herrick | 2024-07-18 06:00
0 | 2 | 82.66 | SF | 3248 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1479758 | 57118 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 9 | 2014-10-05 | 3 | 68.75 | 919983.54 | 510462.34 | 4 | 55.26 | 1317215.88 | 2943947.33 |  | 2024-08-18 22:43 | 2024 | 2029 | 2 | Overhead cover for Virtual Convoy Trainer. No lighting; structural paint peeling. |  | Jeffrey | Herrick | 2024-04-30 06:00
0 | 2 | 82.66 | SF | 6611 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295816 | 47429 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 21 | 2003-09-21 | 4 | 45.45 | 3268706.5 | 1038998.31 | 4 | 34.04 | 3952189.8 | 5992129.24 |  | 2024-04-30 17:50 | 2024 | 2029 | 2 | HEMMIT refueler parking; vehicles do not fit under protective structure.Allows snow and rain onto vehiclesNo security measures.Inadequate lighting interior and exterior. |  | Jeffrey | Herrick | 2024-04-30 06:00
0 | 2 | 82.11 | SF | 2160 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 294926 | 47645 | Operation & Training | Land Operational Facilities | Airfield Operational Buildings | Aviation Operations Building | 14112 | Avn Unit Ops | 36 | 1988-07-01 | 4 | 53.5 | 1462899.77 | 562782.74 | 4 | 40.61 | 1868565.24 | 3146021.02 |  | 2023-04-25 18:30 | 2023 | 2028 | 2 | Was categorized as Administrative; under renovation for Airfield ManagementPoor lighting and drainage.Not ADA/Handicap accessible.No Loading dock or ramp.No classrooms or conference area.No security measures. |  | Jeffrey | Herrick | 2023-04-18 06:00
0 | 2 | 80.42 | SF | 1465 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190980 | 47436 | Utility & Ground Improvements | Miscellaneous Utilities | Miscellaneous Utilities - Squa | Utility Building | 89144 | Wtr Sup Bld Np | 66 | 1958-09-01 | 4 | 57.66 | 479124.47 | 221599.68 | 4 | 45.21 | 620015.53 | 1131611.87 |  | 2024-05-07 18:41 | 2024 | 2029 | 2 | The Building and the Fire protection system it supports does not meet current code requirements and is in a failing state.Cannot adequately support Bryant Army Airfield hangar deluge system requirements.Need MILCON to modernize entire system. |  | Jeffrey | Herrick | 2024-04-30 06:00 | 23 | OW Mission
0 | 3 | 79.5 | SF | 10460 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295818 | 49050 | Supply | Covered Storage | Installation and Organization | Covered Storage Shed, Installa | 44262 | Veh Str Shed In | 25 | 1998-10-08 | 4 | 46.03 | 2859707.07 | 1086037.77 | 4 | 34.2 | 3486592.26 | 5298697.56 |  | 2024-05-02 15:33 | 2024 | 2029 | 2 | Open sided lean-to structure.Poor lighting and drainageNo fire suppression.Minimal electrical capability |  | Jeffrey | Herrick | 2024-05-01 06:00
0 | 2 | 83.99 | SF | 800 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 606425 | 49000 | Operation & Training | Training Facilities | Training Buildings | Applied Instruction Building | 17136 | Auto-Aid Inst | 33 | 1991-06-17 | 3 | 72.22 | 290583.3 | 167433.51 | 4 | 58.65 | 432480.86 | 1046016.19 |  | 2024-08-19 14:52 | 2024 | 2029 | 2 |  |  | Jeffrey | Herrick | 2024-07-01 06:00
0 | 3 | 77.52 | SF | 4300 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295820 | 47428 | Supply | Covered Storage | Installation and Organization | Covered Storage Shed, Installa | 44262 | Veh Str Shed In | 48 | 1976-01-01 | 4 | 51.04 | 1066466.73 | 489625.48 | 4 | 37.43 | 1363008.29 | 2178240.87 |  | 2024-01-18 16:42 | 2024 | 2029 | 2 | Facility is used for equipment maintenance and equipment storage; miscoded for Vehicle Storage. Poor lighting and drainage.Needs an admin area for maintainers.Exterior doors need replacement.No Loading dock or ramp.Limited MHE capability.No latrines or waterNo standby power generator.No security measures.Poorly insulated; no energy management systems |  | Jeffrey | Herrick | 2024-01-17 06:00
0 | 3 | 74.68 | SF | 11012 | 020NG | Alaska National Guard | 1821 | FXSB0001 | ELMENDORF AFB SITE 1 | ELMENDORF AIR FORCE BASE | 423648 | 9311 | Maintenance & Production | Maintenance Facilities | Aircraft Maintenance Facilitie | Aircraft Maintenance Hangar | 21114 | Ac Maint Bay | 26 | 1998-01-01 | 4 | 52.44 | 6902839.3 | 3674679.38 | 4 | 39.05 | 8846780.5 | 14513959.84 |  | 2020-05-22 19:57 | 2020 | 2025 | 2 | Poor lighting and drainage.No Loading dock or ramp.No lobby; inadequate latrines for population and passengers.Limited MHE capability.No standby power generator.No security measures.No secure storage.No proper Admin area ; windows in poor condition windows. |  | Jeffrey | Herrick | 2020-05-20 06:00 | 25 | Incomplete Rating
0 | 3 | 66.79 | SF | 576 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295787 | 57224 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 82 | 1942-01-01 | 4 | 38.78 | 321232.46 | 174241.74 | 4 | 20.98 | 414635.11 | 524718.17 |  | 2022-07-18 16:34 | 2022 | 2027 | 2 | Dilapidated Quonset hut; no utilities, failing structure, no material handling capability; needs demolished. |  | Jeffrey | Herrick | 2022-07-07 06:00 | 25 | Incomplete Rating
0 | 3 | 66.74 | SF | 100 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191204 | 49045 | Operation & Training | Land Operational Facilities | Operational Support Buildings | Miscellaneous Operations Suppo | 14165 | Fuel/Pol Bldg | 33 | 1991-07-01 | 4 | 43.14 | 76922.06 | 45001.02 | 4 | 21.58 | 106082.42 | 135283.25 |  | 2024-05-01 22:40 | 2024 | 2029 | 2 | Concrete Masonry Unit Support structure; has no lighting, no interior electric, no heat, doors are failing. |  | Jeffrey | Herrick | 2024-05-01 06:00
1 | 1 | 95.17 | SF | 1251 | 020NG | Alaska National Guard | 6439 | 02D92 | Alcantra Armory | Palmer | 370767 | 2 | Housing & Community | Unaccompanied Personnel Housin | Unaccompanied Personnel Housin | Dining Facility | 72210 | Dining Facility | 64 | 1960-01-01 | 4 | 51.55 | 1729451.71 | 173610 | 4 | 48.48 | 1839205.22 | 3569559.78 | 2022-05-16 | 2024-08-16 23:20 | 2024 | 2027 | 2 | Poor lighting and drainage.No Loading dock or ramp.No lobby limited admin area.Small kitchen/serving area.No standby power generator.No security measures.Exterior wood siding is rottingNo sprinklers or fire systemsCannot access storage are from inside facility |  | Jeffrey | Herrick | 2024-08-16 06:00 | 10, 34 | Historic, SMS Complete
1 | 1 | 95.09 | SF | 3734 | 020NG | Alaska National Guard | 6439 | 02D92 | Alcantra Armory | Palmer | 370768 | 3 | Supply | Covered Storage | Installation and Organization | Vehicle Storage, Covered | 44263 | Veh Stor Inst | 36 | 1988-01-01 | 4 | 58.22 | 740461.34 | 85230 | 4 | 55.1 | 795707.02 | 1772286.59 | 2022-05-10 | 2023-07-05 11:54 | 2023 | 2028 | 2 | Site is poorly lit, bad drainage.Unpaved lot.Needs bollards.No security measures; no smart sensors.No loading ramp.No fire panel or pull station.Cannot support MHE or all storage operations.No SIPR or NIPR connectivity. |  | Jeffrey | Herrick | 2023-07-03 06:00 | 34, 35 | SMS Complete, Mixed UOM Excluded
1 | 1 | 92.55 | SF | 4850 | 020NG | Alaska National Guard | 6439 | 02D92 | Alcantra Armory | Palmer | 370762 | 7 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 64 | 1960-01-01 | 4 | 58.73 | 3674047.38 | 614420 | 4 | 53.77 | 4115970.61 | 8902465.17 | 2022-05-10 | 2021-08-04 11:37 | 2021 | 2026 | 2 | Should be classified as an administrative facility.Building is ground level, poorly lit, poor drainage and unpaved.50 year old building with uneven foundation.No lobby area.Stairs to mech room not non-skid.Admin, classroom and assembly area do not meet minimum space standards.No arms room.No security systems.Inadequate unit storage space.New roof, windows and insulation |  | Jeffrey | Herrick | 2021-08-03 06:00 | 34 | SMS Complete
1 | 2 | 88.82 | SF | 640 | 020NG | Alaska National Guard | 6439 | 02D92 | Alcantra Armory | Palmer | 370759 | 11 | Supply | Covered Storage | Installation and Organization | Covered Storage Shed, Installa | 44262 | Veh Str Shed In | 21 | 2003-09-29 | 4 | 57.14 | 198318.65 | 51716.39 | 4 | 49.95 | 231585.28 | 462712.68 |  | 2021-08-05 11:56 | 2021 | 2026 | 2 | HEMTT Shed.Square footage should be 1,080 not 640.Site is poorly lit, does not drain.Parking lot is unpaved.No loading dock.No water, electrical outlets, LAN, or comm.No central alarm or detectors; only extinguishers are truck-mounted.No security systems.Small truck area and does not support MHE; space is inadequate and front of structure is unsided, exposing vehicles to wind/snow/rain. |  | Jeffrey | Herrick | 2021-08-03 06:00 | 25 | Incomplete Rating
1 | 2 | 83.48 | SF | 17167 | 020NG | Alaska National Guard | 6439 | 02D92 | Alcantra Armory | Palmer | 370761 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 50 | 1974-01-01 | 3 | 64.93 | 11603473.56 | 5063900 | 4 | 53.4 | 15419917.77 | 33086608.37 | 2022-05-19 | 2024-08-16 22:56 | 2024 | 2027 | 2 | The armory doesn't meet current 415-12 space requirements for the number of units stationed there. Poor lighting and drainage on perimeter that don't meet the ATFP security lighting standards.Organizational parking is unpaved and very undersized. Bathrooms do not meet all of the "4-L" requirements. Existing Arms room door not marked "Class V", but meets criteria. The Armory doesn't have enough vault space to meet the units requirements.Undersized classroom space/ learning center; no zonal lighting. currently using the corning of the main administrative area for this function. No sprinkler system or stand pipe for fire protection.No loading dock or vehicle maintenance space at facility.overwrite is per 1390/91 analysis. |  | Jeffrey | Herrick | 2024-08-16 06:00 | 10, 23, 34 | Historic, OW Mission, SMS Complete
2 | 1 | 92.33 | SF | 14710 | 020NG | Alaska National Guard | 6471 | 02B60 | Kenai Armory | Kenai | 1032284 | 2 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 51 | 1973-01-01 | 3 | 66.2 | 9126366.76 | 1920030 | 3 | 60.79 | 10587593.26 | 27001085.09 | 2019-06-04 | 2024-07-11 14:33 | 2024 | 2029 | 2 | Latrine renovation project complete for male and female soldiers; however arms vault was demolished for needed space.Poor exterior lighting; site incompatible with residential zoning and no expansion capabilityAs a shelter-in-place facility it is inaccessible to disabled.No loading Dock. Kitchen is undersized and not commercial grade.Has adequate storage space for mission after renovating maintenance bay for storage; however, now has no bay for organizational equipment or maintenance.Vehicle maintenance area is outside and severely limits any maintenance activities;No sprinklers or central fire panelAdmin space inadequate and undersized for army requirements.No dedicated standby power generator; portable generator is available but not wired into automatic transfer switch.Roof has standing water and no heat trace in drains. |  | Jeffrey | Herrick | 2024-07-10 06:00 | 34 | SMS Complete
2 | 2 | 85.62 | SF | 1200 | 020NG | Alaska National Guard | 6477 | 02B85 | Kodiak Armory | Kodiak | 369630 | 2 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 23 | 2001-01-22 | 4 | 47.13 | 594392.4 | 159950 | 4 | 37.79 | 699452.56 | 1124252.7 | 2019-05-13 | 2022-08-15 12:39 | 2022 | 2027 | 2 | Unpaved, poorly lit, bad drainage.No standoff; no room for expansion.No loading dock.Unpaved, poor truck area; very constrained.Steel laddder does not meet OSHA standads.Only controlled entry measures is padlock on gate, and it is being left open.No water to facility for operations; no floor drainsNo standby power generator.Cannot support MHE; limited storage and movement.No comm or NIPR. |  | Jeffrey | Herrick | 2022-08-10 06:00 | 25, 34 | Incomplete Rating, SMS Complete
2 | 3 | 64.06 | SF | 8426 | 020NG | Alaska National Guard | 6477 | 02B85 | Kodiak Armory | Kodiak | 369633 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 65 | 1959-01-01 | 3 | 66.67 | 3739041.83 | 3744490 | 4 | 41.18 | 6599107.21 | 11218247.3 | 2019-05-13 | 2022-08-15 12:49 | 2022 | 2027 | 2 | Site location is marginal, constrained, limited disabled access and no standoff due to lot configuration. Front parking area is unpaved and poorly lit.Exterior door hinges are exposed and corroding.No Loading dock or truck area nor bollards to protect overhead door jambs.New Roof system in place.Kitchen is residential, not commercial grade.No security systems for parking or armory.Assembly area is just under 5400sf.Arms room ceiling un-reinforced and has 400 square inch ventilator opening; door is not marked as Class V, two walls are un-reinforced CMU.Classroom and Unit Storage space does not meet Army minimum space standards.Needs a mop sink.No standby power generator. |  | Jeffrey | Herrick | 2022-08-10 06:00 | 34 | SMS Complete
3 | 2 | 83.99 | SF | 800 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 606425 | 49000 | Operation & Training | Training Facilities | Training Buildings | Applied Instruction Building | 17136 | Auto-Aid Inst | 33 | 1991-06-17 | 3 | 72.22 | 290583.3 | 167433.51 | 4 | 58.65 | 432480.86 | 1046016.19 |  | 2024-08-19 14:52 | 2024 | 2029 | 2 |  |  | Jeffrey | Herrick | 2024-07-01 06:00
3 | 2 | 87.85 | SF | 168455 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 606425 | 49000 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17142 | Arng/Usar Ctr | 33 | 1991-06-17 | 2 | 80.67 | 34235097.96 | 21521408.71 | 3 | 70.48 | 52290812.68 | 177108628.85 |  | 2021-08-20 16:46 | 2021 | 2026 | 2 | The armory doesn't meet current 415-12 space requirements for the number of units stationed there. Some signs of standing water on roof. Organizational parking is undersized. Bathrooms do not meet all of the "4-L" requirements. Existing Arms room door not marked "Class V", but meets criteria. The Armory doesn't have enough vault space to meet the units requirements. Undersized classroom space/ learning center; no zonal lighting. Standby generator only provides for 25%of space and operations. Unit storage space is constrained, inconvenient and cannot meet unit needs.No Energy Management system nor smart sensors/meters installed. |  | Jeffrey | Herrick | 2021-08-20 06:00
4 | 1 | 95.86 | SF | 7704 | 020NG | Alaska National Guard | 5673 | 02B41 | Juneau Armory And Fms | Juneau | 336591 | 2 | Maintenance & Production | Maintenance Facilities | Tank and Automotive Maintenanc | Vehicle Maintenance Shop, Nati | 21407 | Arng Veh Maint | 19 | 2005-08-01 | 3 | 68.6 | 4589085.9 | 593850 | 3 | 65.57 | 5031827.83 | 14614923.25 | 2019-06-06 | 2022-12-15 15:46 | 2023 | 2028 | 2 | Poor site drainage; snow & rain accumulate at base of building, impeding operations.Limited parking, poor lot lighting.No lobby area.No loading dock, ramp facilities.Security system inop; needs repaired, data reloaded in card reader.No SIPR connection.No SCIF/EOC facility.No Emergency or Stand-by power generator.Not ADA compliant |  | Jeffrey | Herrick | 2022-12-14 06:00 | 34 | SMS Complete
4 | 1 | 92.98 | SF | 24519.5 | 020NG | Alaska National Guard | 5673 | 02B41 | Juneau Armory And Fms | Juneau | 336592 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 19 | 2005-07-08 | 3 | 77.78 | 7253693.81 | 2187179.87 | 3 | 72.19 | 9077174.75 | 32644886.63 | 2019-06-07 | 2021-03-23 16:54 | 2021 | 2026 | 2 | Energy; no remote sensoring nor smart metering for gas or electric.Site is severely constrained for parking, traffic and zero expansion.Roof leaks, has standing water: rubber has deteriorated & drains are in high areas; needs re-design.Drill hall floor is partnered with local university yet is only available for drill 2 days of the month.Arms room floor is not 6" of re-inforced concrete.Admin & Classroom space lost to State's Department of Administrative ServicesElevator inspection/certification is now updated.75% of square footage is predominately used by the university; multipurpose classroom area less than 800 s.f. |  | Jeffrey | Herrick | 2021-03-18 06:00 | 34 | SMS Complete
4 | 2 | 85.69 | SF | 16954 | 020NG | Alaska National Guard | 6466 | 02B43 | Juneau AAOF | Juneau | 562812 | 1 | Maintenance & Production | Maintenance Facilities | Aircraft Maintenance Facilitie | Aircraft Maintenance Hangar | 21114 | Ac Maint Bay | 35 | 1989-01-01 | 4 | 59.22 | 9433396.85 | 3155665.17 | 4 | 51.29 | 11267700.53 | 23132410.12 | 2019-05-31 | 2021-06-22 12:49 | 2021 | 2026 | 2 |  |  | Jeffrey | Herrick | 2021-03-18 06:00 | 25, 34 | Incomplete Rating, SMS Complete
4 | 2 | 83.48 | SF | 10000 | 020NG | Alaska National Guard | 5673 | 02B41 | Juneau Armory And Fms | Juneau | 1070898 | 3 | Supply | Covered Storage | Installation and Organization | Controlled Humidity Storage, I | 44230 | Contr Hum Wh In | 17 | 2006-11-01 | 4 | 49.48 | 1956118.77 | 628700 | 4 | 37.74 | 2410651.62 | 3871969.07 | 2019-06-05 | 2024-05-09 17:18 | 2024 | 2029 | 2 | Being used as the local ACFT fitness area; needs unit heaters and insulation.Poor lighting, poor drainage, no signage.Limited parking and access; constrained truck area. No loading dock, or ramp to unload equipment. No water nor sewage, no latrines.No fire detection or suppression systems except 4 extinguishers.Unheated.Limited storage capability; lacks room for MHE, storage bins, dunnage.No SIPR/NIPR connections, no LAN, No comm |  | Jeffrey | Herrick | 2024-05-09 06:00 | 34 | SMS Complete
4 | 2 | 81.8 | SF | 2500 | 020NG | Alaska National Guard | 6466 | 02B43 | Juneau AAOF | Juneau | 556188 | 3 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 21 | 2003-09-29 | 4 | 56.06 | 1030725.61 | 426962.43 | 4 | 43.18 | 1332956.36 | 2345756.96 |  | 2024-08-15 22:36 | 2024 | 2029 | 2 | Protective roof covering decommissioned fuel facility. Sides open to elements. Corrosion and cracking evident. |  | Jeffrey | Herrick | 2024-05-08 06:00
4 | 3 | 78.46 | SF | 1980 | 020NG | Alaska National Guard | 6466 | 02B43 | Juneau AAOF | Juneau | 1179127 | 6 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 11 | 2013-09-24 | 4 | 54.39 | 847360.6 | 400193.67 | 4 | 39.32 | 1127279.43 | 1857839.51 |  | 2024-08-19 14:42 | 2024 | 2029 | 2 | Structure is roof with open chain link fence siding;no security measures, backup power and very constrained vehicle access and maneuver area.Provides limited weather protection to decommissioned fuel tanks. |  | Jeffrey | Herrick | 2024-05-15 06:00
4 | 3 | 75.09 | SF | 235 | 020NG | Alaska National Guard | 6466 | 02B43 | Juneau AAOF | Juneau | 556187 | 2 | Operation & Training | Land Operational Facilities | Operational Support Buildings | Miscellaneous Operations Suppo | 14165 | Fuel/Pol Bldg | 35 | 1989-01-01 | 4 | 56.86 | 141977.98 | 85000 | 4 | 38.47 | 202494.46 | 329109.84 | 2019-05-31 | 2024-05-09 17:01 | 2024 | 2029 | 2 | Fuel Facility has been decommissioned for several years; non-operational , has no aviation fuel.10'x20' support building shed.Doors and exterior degrading rapidly |  | Jeffrey | Herrick | 2024-05-08 06:00 | 34 | SMS Complete
4 | 4 | 6.81 | SF | 64 | 020NG | Alaska National Guard | 6466 | 02B43 | Juneau AAOF | Juneau | 1168761 | 4 | Operation & Training | Land Operational Facilities | Operational Support Buildings | Miscellaneous Operations Suppo | 14165 | Fuel/Pol Bldg | 35 | 1989-01-01 | 4 | 56.86 | 38666.34 | 86600 | 4 | 0 | 100321.96 | 89629.91 | 2019-05-31 | 2024-06-12 23:35 | 2024 | 2029 | 2 | Wooden storage shed 8'x20' adjacent to POL structures.Fuel Facility has been decommissioned for several years; non-operational, has no fuel.Doors and exterior are corroding; provides minimal protection. |  | Jeffrey | Herrick | 2024-05-15 06:00 | 34 | SMS Complete
4 | 2 | 88.91 | SF | 15305 | 020NG | Alaska National Guard | 6521 | 02D24 | Sitka Armory | Sitka | 368339 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 54 | 1970-01-01 | 3 | 61.08 | 7930667.1 | 2098290 | 4 | 53.54 | 9466551.71 | 20376842.51 | 2019-09-08 | 2024-03-11 16:09 | 2024 | 2029 | 2 | Location Comment: Armory sits by the ocean / nice view / good community location, commercial zone.EHSP Comments: Due to location heating tank should probably have an additional dike installed.No disabled access; dumpster not screened - too close to building / utilities are overhead; one area tested above 40 mg lead.Building Elevation too low; poor drainage, roof discharge ponds at foundation.Parking area is not up to current standards; unpaved, poorly lit, no standoff & no signage.Kitchen has no hood over stove, no dishwasher; residential grade.Exterior door hinges exposed.No loading dockNot enough security measures or standoff.Walls need to be repairedNo female locker room at latrine.No emergency power / no switching device.Assembly area does not meet minimum space of 5400 sq. ft.Project to replace metal roof and siding to commence summer 2019. |  | Jeffrey | Herrick | 2023-11-29 06:00 | 34 | SMS Complete
4 | 2 | 86.84 | SF | 1500 | 020NG | Alaska National Guard | 6476 | 02B70 | Klawock Armory | Klawock | 369628 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 23 | 2000-12-05 | 4 | 50.63 | 985956.92 | 243990 | 4 | 42.34 | 1151490.8 | 1997077.02 | 2019-05-02 | 2024-04-26 20:18 | 2024 | 2029 | 2 | Klawock armory; located adjacent to airport.Poor lighting and drainage.Unpaved parking area.Exterior doors have corrosion and need maintenance.Does not meet minimum space for administrative areas.Classroom and unit storage do not meet Army standards for readiness centers.No assembly area nor loading dock nor arms vault.No water nor sewer.Fire detectors inoperable and extinguishers are out of date.Floor tiles are popping at perimeter walls.No security measures or standby power generation. |  | Jeffrey | Herrick | 2024-04-25 06:00 | 34 | SMS Complete
4 | 3 | 75.75 | SF | 700 | 020NG | Alaska National Guard | 6521 | 02D24 | Sitka Armory | Sitka | 1487608 | 2 | Supply | Covered Storage | Installation and Organization | Vehicle Storage, Covered | 44263 | Veh Stor Inst | 54 | 1970-01-01 | 4 | 59.44 | 97744.12 | 58435.37 | 4 | 43.53 | 136093.66 | 240986.49 |  | 2022-08-30 16:42 | 2022 | 2027 | 2 | Poor drainage and lighting.Constrained truck area.No plumbing nor latrines.HVAC is inefficient unit heaters.No security systems.No fire panel nor suppression systems.No loading dock nor ramp; very limited MHE capability. |  | Jeffrey | Herrick | 2022-08-25 06:00 | 25 | Incomplete Rating
4 | 3 | 75.52 | SF | 18446 | 020NG | Alaska National Guard | 6472 | 02B65 | Ketchikan Armory | Ketchikan | 369625 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 62 | 1962-01-01 | 3 | 64 | 8841139.84 | 5582340 | 4 | 46.99 | 13018523.48 | 24558721.78 | 2019-06-25 | 2024-04-26 20:11 | 2024 | 2029 | 2 | Major restoration project underway; latrines am showers and locker rooms are being expanded and modernized; only one small latrine available in the interim. Armory sited in residential area.No smart meters or HVAC sensors. Security cameras lack overall coverage.Repaired roof still has minor leaks on west side parapet wall.Exterior door hinges exposedNo proper lobby.No loading Dock. Lobby is dated and needs maintenance/repair project. Unit Supply & storage does not meet minimum space standardsClassroom space 50% of 1500 sq ft minimum requirement and no zonal lighting or A/V capability.Vehicle Maintenance area is suitable only for minor work and inspection.Energy Ratings: envelope and heating system older than 10 years; no smart metering; no alternative fuels.No Kitchen or breakroom available.Fire Extinguishers are out of date.No emergency power generator. |  | Jeffrey | Herrick | 2024-04-24 06:00 | 34 | SMS Complete
4 | 0 |  | SF | 14400 | 020NG | Alaska National Guard | 6468 | 02B45 | Ng Juneau Oms | Juneau | 1002691 | 1 | Maintenance & Production | Maintenance Facilities | Tank and Automotive Maintenanc | Vehicle Maintenance Shop, Nati | 21407 | Arng Veh Maint | 74 | 1950-01-01 | 0 |  |  | 0 |  |  |  | 12388940.38 |  | 2024-04-11 17:56 | 2024 | 2029 | 2 | NA Rating. Facility is disposed. Facility and site were divested in 2009; no longer on FISP. Needs to be removed from PRIDE and HQIIS. |  | Jeffrey | Herrick | 2024-04-11 06:00 | 37, 39, 40 | All Q&amp;F are NA, All Q NA, All F NA
5 | 1 | 91.08 | SF | 4354 | 020NG | Alaska National Guard | 6456 | 02B05 | Fairbanks Armory | Fairbanks | 365865 | 2 | Maintenance & Production | Maintenance Facilities | Tank and Automotive Maintenanc | Vehicle Maintenance Shop, Nati | 21407 | Arng Veh Maint | 56 | 1968-01-01 | 4 | 49.4 | 4283700.03 | 740730 | 4 | 43.89 | 4749829.51 | 8465810.34 | 2019-06-27 | 2022-10-17 13:13 | 2023 | 2028 | 2 | Location Comment: Building in small, constrained area.Poor lighting, bad drainage, small truck area.No loading dock adjacent (over 150 meters away).One toilet for all personnel / no shower facility / locker is in with parts room.Hook up for emergency power is present but no generator.No sprinkler or standpipe system / fire panel and pull stations present along with fire extinguishers.No Lift / crane needs upgraded from 3 Ton / battery exhaust fan needs upgraded.No SIPR/SCIF/EOC facilities.No centralized wash area; in adjacent facility and is constrained are-wise.Overhead doors & vehicle service area do not meet Army standards.No security systems in place.No emergnecy or dedicated stand-by power.Parking inadequate for organizational vehicles. |  | Jeffrey | Herrick | 2022-10-12 06:00 | 34 | SMS Complete
5 | 2 | 87.85 | SF | 1716 | 020NG | Alaska National Guard | 6456 | 02B05 | Fairbanks Armory | Fairbanks | 365866 | 3 | Supply | Covered Storage | Installation and Organization | Covered Storage Shed, Installa | 44262 | Veh Str Shed In | 21 | 2003-09-29 | 4 | 37.04 | 580695.27 | 112066.8 | 4 | 30.58 | 640288.22 | 922324.12 |  | 2023-12-05 00:24 | 2024 | 2029 | 2 | Facility is open-sided, covered storage. Parking lot has been recently paved but slope causes ice buildup in winter conditions.Very limited storage capability due to exposure to arctic weather and elements.Loading ramp not adjacent to facility and in very poor condition.No running water or sewage.No Comms.Structural columns have been damaged due to lack of protecting bollards.No fire protection.No standby/emergency power. |  | Jeffrey | Herrick | 2023-11-16 06:00
5 | 2 | 82.15 | SF | 30424 | 020NG | Alaska National Guard | 6456 | 02B05 | Fairbanks Armory | Fairbanks | 365864 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 62 | 1962-01-01 | 3 | 66.45 | 13928753 | 6870896.71 | 4 | 53.83 | 19167888.63 | 41516402.39 | 2019-06-27 | 2023-11-28 15:54 | 2024 | 2029 | 2 | Facility doesn't meet the space standards in 415-12 for a single unit and at this time there are multiple units and detachments assigned to the armory. the current renovation is only bring up the Quality of what is there and is not increasing the size of the facility.Fire Alarm Panel trouble with battery fuse and ground; needs repair/replaced and re-certified.Site location is poor for public relations visibility and zero room on-site for expansion.No parking standoff and inadequate spaces: truck area is unpaved.Drill hall floor no longer meets Army space standard since 25% has been blocked off for temporary unit storage.No adequate loading dock at facility.Administrative area barely meets one Company size requirement and not enough for the Detachments.Unit equipment and MTOE supply area requirements are inadequate.Classroom areas meet only 85% of Company size unit requirements.Fitness room converted from needed Admin space; temporary and not enough room for ACFT.No emergency or dedicated stand-by power.Lacks security measures. Not handicap accessible. |  | Jeffrey | Herrick | 2023-11-16 06:00 | 34 | SMS Complete
5 | 4 | 55.78 | SF | 7456 | 020NG | Alaska National Guard | 6532 | 02D80 | Valdez Armory | OLD VALDEZ | 561182 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 36 | 1988-01-01 | 4 | 54.66 | 4500813.01 | 4078660.02 | 4 | 25.97 | 7348378.29 | 9926804.16 | 2019-05-06 | 2020-06-26 11:08 | 2020 | 2025 | 2 | Poor site drainage.Parking areas are unpaved, no standoff, poorly lit.Severe cracking of foundation slab (drill hall and arms room).No loading dock.No lobby.No security measures.Arms room door requires waiver; no security light.Inadequate unit storage.No sprinklers or standpipes.No exhaust hood or suppression in kitchen.Classroom area space barely meets AK minimum standard.Assembly hall space does not meet minimum standard (is used for vehicle storage also).No emergency power or UPS (critical comm antennae can be damaged if power outage)AT assessment performed 31 Jul 18 |  | Jeffrey | Herrick | 2020-06-24 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 4 | 4.47 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295784 | 49204 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 26 | 1998-01-01 | 4 | 53.8 | 1683470.8 | 1003600 | 4 | 36.75 | 2304709.45 | 3643876.2 | 2018-05-11 | 2021-06-24 17:13 | 2021 | 2026 | 2 | Poor lighting and drainage.No water/sewer connections.No loading dock or ramp.No additional security measures.No centralized fire alarm system.Constrained truck area; limited Material Handling Equipment capability. |  | Jeffrey | Herrick | 2021-06-24 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 1 | 99.38 | SF | 20000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190972 | 49203 | Supply | Covered Storage | Installation and Organization | Controlled Humidity Storage, I | 44230 | Contr Hum Wh In | 34 | 1990-07-01 | 3 | 61.21 | 2901701.03 | 36350 | 3 | 60.83 | 2929818.26 | 7480538.88 | 2018-05-16 | 2021-05-12 16:11 | 2021 | 2026 | 2 | Poor lighting.Poor drainage.No loading dock or ramp.Constrained Truck Area. |  | Jeffrey | Herrick | 2021-04-26 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 1 | 98.98 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1201043 | 47435 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 10 | 2014-01-07 | 3 | 60.82 | 1427670.7 | 10600 | 3 | 60.63 | 1434716.16 | 3643876.2 | 2018-06-08 | 2021-06-25 14:21 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.No standby power generator. |  | Jeffrey | Herrick | 2021-06-25 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 1 | 98.81 | SF | 5000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1201039 | 57408 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 10 | 2014-01-07 | 4 | 52.38 | 2169017.31 | 12400 | 4 | 52.21 | 2176585.13 | 4554845.25 | 2018-05-09 | 2024-04-22 22:30 | 2024 | 2029 | 2 | Poor lighting and drainage.No lobby and no windowsNo Loading dock or ramp.Limited MHE capability.No standby power generator.No security systems. |  | Jeffrey | Herrick | 2024-04-22 06:00 | 34 | SMS Complete
6 | 1 | 98.42 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1268039 | 49198 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 9 | 2014-12-09 | 4 | 55.19 | 1632820.93 | 17900 | 4 | 54.88 | 1644056.8 | 3643876.2 | 2018-06-08 | 2024-04-18 19:19 | 2024 | 2029 | 2 | Has no controlled humidity unit; 4 unit heaters only.Poor drainage and lighting exterior.No loading ramp, no dunnage poor MHE capability.No security measure or fire suppression.No loading dock or ramp.No admin area.No NIPR or LAN or phones. |  | Jeffrey | Herrick | 2024-04-18 06:00 | 34 | SMS Complete
6 | 1 | 98.37 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1201042 | 57116 | Operation & Training | Training Facilities | Simulation Facilities | General Purpose Simulator Faci | 17211 | Sim Bld Non-Mot | 10 | 2014-01-07 | 4 | 51.18 | 3681992.84 | 54890 | 4 | 50.65 | 3721844.03 | 7541976.33 | 2018-05-09 | 2022-12-06 13:51 | 2023 | 2028 | 2 | No lobby or loading dock.Inadequate Tactical Automation, Video Teleconferencing and Conference rooms.Inadequate administrative, storage and Director of Operations areas.No Soldier storage or Mud rooms. |  | Jeffrey | Herrick | 2022-12-05 06:00 | 34 | SMS Complete
6 | 1 | 95.72 | SF | 5000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1201036 | 57400 | Operation & Training | Training Facilities | Training Buildings | Organizational Classroom | 17119 | Org Classroom | 10 | 2014-01-07 | 4 | 44.59 | 4020535.43 | 90950 | 4 | 43.68 | 4086383.13 | 7255974.42 | 2018-05-09 | 2024-04-22 22:46 | 2024 | 2029 | 2 | Facility recently constructed but not complete nor useable.Used as unit storage; has no organizational classroom capability, equipment or function.Essentially is a heated, sprinklered warehouse with a latrine yet lacks overhead doors.Substantially incomplete. |  | Jeffrey | Herrick | 2024-04-22 06:00 | 34 | SMS Complete
6 | 1 | 94.92 | SF | 20000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190971 | 49201 | Supply | Covered Storage | Installation and Organization | Controlled Humidity Storage, I | 44230 | Contr Hum Wh In | 19 | 2005-07-01 | 3 | 65.52 | 2579289.81 | 298000 | 3 | 62.36 | 2815954.97 | 7480538.88 | 2018-05-01 | 2021-05-12 16:08 | 2021 | 2026 | 2 | No loading dock/ramp.Constrained truck area.Poor lighting and drainage |  | Jeffrey | Herrick | 2021-04-26 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 1 | 94.84 | SF | 20000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190973 | 49205 | Supply | Covered Storage | Installation and Organization | Controlled Humidity Storage, I | 44230 | Contr Hum Wh In | 34 | 1990-07-01 | 3 | 63.03 | 2765555.22 | 302350 | 4 | 59.87 | 3002023.99 | 7480538.88 | 2018-05-01 | 2021-05-12 16:14 | 2021 | 2026 | 2 | Poor lighting.Poor drainage.No loading dock or ramp.Constrained Truck Area. |  | Jeffrey | Herrick | 2021-04-26 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 1 | 93.86 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 994758 | 47424 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 16 | 2008-09-26 | 4 | 43.86 | 2045672.1 | 63950 | 4 | 42.87 | 2081603.27 | 3643876.2 | 2018-05-22 | 2023-06-12 16:20 | 2023 | 2028 | 2 | Poor drainage and lighting.Constrained truck area.No plumbing nor latrines.HVAC is inefficient unit heaters.No security systems.No fire panel nor suppression systems.No loading dock nor ramp; very limited MHE capability. |  | Jeffrey | Herrick | 2023-06-12 06:00 | 34 | SMS Complete
6 | 1 | 93.06 | SF | 1161 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191237 | 47431 | Operation & Training | Land Operational Facilities | Airfield Operational Buildings | Aviation Operations Building | 14112 | Avn Unit Ops | 28 | 1996-01-01 | 4 | 55.94 | 745048.56 | 82374.19 | 4 | 52.37 | 805345.04 | 1690986.3 | 2018-06-11 | 2021-03-04 17:30 | 2021 | 2026 | 2 | Poor lighting and drainage.Poor accessibility; not ADA compliant.No security measures.Lacks secure storage; uses Flight Ops building across the street.Multiple heat zones in floors and ceiling are shut off due to leaks or not working.Administrative areas need total restoration.No lobby.Latrines need renovation; occupants lack enough showers and lockers.No Loading dock or ramp.No standby power generator. |  | Jeffrey | Herrick | 2021-03-04 06:00 | 34 | SMS Complete
6 | 1 | 93.06 | SF | 36037 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191237 | 47431 | Maintenance & Production | Maintenance Facilities | Aircraft Maintenance Facilitie | Aircraft Maintenance Hangar | 21114 | Ac Maint Bay | 28 | 1996-01-01 | 4 | 55.07 | 21340508.45 | 2313765.81 | 4 | 52.4 | 22610061.74 | 47497236.71 | 2018-06-11 | 2021-03-04 17:27 | 2021 | 2026 | 2 | Facility is outdated and not sized to adequately house assigned CH-47 aircraft.Poor lighting and drainage.Poor accessibility; not ADA compliant.No security measures. No secure storage; must use adjacent Flight Ops facility.Administrative areas lack comm, SIPR?NIPR and systems furniture.HVAC systems requires major upgrade; HEAT LOSS AND RECOVERY IN WINTER EFFECT OPERATIONS.No lobby area or arctic entry.Lacks storage.Bo Osha certified battery shop.No loading dock nor ramp.No standby emergency power generator |  | Jeffrey | Herrick | 2021-03-04 06:00 | 23, 25, 34 | OW Mission, Incomplete Rating, SMS Complete
6 | 1 | 92.57 | SF | 5000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1185542 | 57114 | Operation & Training | Training Facilities | Training Buildings | General Purpose Instruction Bu | 17120 | Gen Inst Bldg | 10 | 2013-10-23 | 4 | 48.15 | 3762222.74 | 157990 | 4 | 46.4 | 3889278.56 | 7255974.42 | 2018-05-08 | 2022-10-25 11:44 | 2023 | 2028 | 2 | Facility is mis-categorized as General Instruction; actual usage is a Cross-fit gym.Pre-engineered bare facility with minimal insulation.Poor lighting and drainage (snow removal).No loading dock.No lobby nor auditorium.No emergency power.Lacks admin space and storage.No zonal lighting or audio-visual capability.No administrative area nor storage.No security measures.No Windows. |  | Jeffrey | Herrick | 2022-10-10 06:00 | 34 | SMS Complete
6 | 1 | 91.75 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1061698 | 47425 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 14 | 2010-09-07 | 4 | 43.86 | 2045672.1 | 122810 | 4 | 41.97 | 2114674.56 | 3643876.2 | 2018-05-22 | 2023-06-12 16:24 | 2023 | 2028 | 2 | Poor drainage and lighting.Constrained truck area.No plumbing nor latrines.HVAC is inefficient unit heaters.No security systems.No fire panel nor suppression systems.No loading dock nor ramp; very limited MHE capability. |  | Jeffrey | Herrick | 2023-06-12 06:00 | 34 | SMS Complete
6 | 1 | 91.46 | SF | 8000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191244 | 47433 | Supply | Covered Storage | Installation and Organization | Vehicle Storage, Covered | 44263 | Veh Stor Inst | 62 | 1962-09-01 | 3 | 60.12 | 1060988.79 | 554150 | 4 | 46.36 | 1427189.05 | 2660453.34 | 2018-06-12 | 2021-03-24 17:59 | 2021 | 2026 | 2 | Hangar two converted to category code for snow removal equipment vehicle storage |  | Jeffrey | Herrick | 2021-02-02 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 88.83 | SF | 19234 | 020NG | Alaska National Guard | 190444 | 02D95 | Anchorage International Airport | Anchorage | 1137328 | 52 | Operation & Training | Land Operational Facilities | Operational Support Buildings | Security Force Building | 14132 | Ready Bldg | 12 | 2012-04-21 | 3 | 61.23 | 6499505.16 | 1836250 | 4 | 53.25 | 7837260.98 | 16764264.01 | 2019-05-30 | 2024-08-14 17:25 | 2024 | 2029 | 2 | Used by Civil Support Team.Facility lacks admin space; storage areas temporarily converted to office space with systems furniture.No Smart Metering for utilities.No standby or emergency power.Classrooms lack zonal lighting and A/V capability.Arms room is 9mm in safe only (no ammo storage); no Class V doors nor reinforced concrete walls/ceilings.Conference room is inadequate.Needs increased storage; storage is in open maintenance bays.Facility under renovation; modernization includes additional admin and classroom space and a mezzanine; ECD is Fall/Winter 2024 |  | Jeffrey | Herrick | 2024-07-31 06:00 | 34 | SMS Complete
6 | 2 | 88.16 | SF | 10200 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190974 | 49150 | Maintenance & Production | Maintenance Facilities | Tank and Automotive Maintenanc | Vehicle Maintenance Shop, Nati | 21407 | Arng Veh Maint | 22 | 2002-01-15 | 3 | 67.44 | 6086054.57 | 1323426.51 | 3 | 62.22 | 7062311.64 | 18691813.8 | 2018-05-11 | 2024-05-02 15:19 | 2024 | 2029 | 2 | Inadequate drainage and snow removal.No loading dock.Not ADA compliant.Area has card reader but facility has no systems.Roof restoration project underway; will be completed end of FY24No emergency power generator on standby.Limited secure storage.Overhead doors do not meet 14'x24' Army Standard; crane is 7 tons, slightly undersized and accesses 60% of floor.No laundry room or showers. |  | Jeffrey | Herrick | 2024-05-01 06:00 | 34 | SMS Complete
6 | 2 | 88.16 | SF | 57800 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190974 | 49150 | Maintenance & Production | Maintenance Facilities | Tank and Automotive Maintenanc | Vehicle Maintenance Shop, Nati | 21419 | Csms/Mates | 22 | 2002-01-15 | 2 | 80.23 | 16766228.78 | 6004503.49 | 3 | 74.44 | 21680386.49 | 84806417.72 | 2018-05-11 | 2021-08-19 18:23 | 2021 | 2026 | 2 | Inadequate drainage and snow removal.Not handicap accesible.Structural column has diagonal failure cracking (possibly earthquake damage)No loading dock.No emergency power generator on standby.Overhead doors do not meet 14'x24' Army Standard.No Laundry/Utility area. |  | Jeffrey | Herrick | 2021-08-19 06:00 | 34 | SMS Complete
6 | 2 | 88.07 | SF | 1200 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295800 | 57468 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 31 | 1993-07-01 | 4 | 44.7 | 600565.08 | 37600 | 4 | 42.46 | 624852.4 | 1086012.81 | 2018-05-06 | 2021-06-25 14:13 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.Unheated; no water.No standby power generator. |  | Jeffrey | Herrick | 2021-06-25 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 88.07 | SF | 1200 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295799 | 57466 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 31 | 1993-07-01 | 4 | 44.7 | 600565.08 | 37600 | 4 | 42.46 | 624852.4 | 1086012.81 | 2018-05-06 | 2021-06-25 14:08 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.Unheated; no water.No standby power generator.No water/sewer connections.No fire alarm system. |  | Jeffrey | Herrick | 2021-06-25 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 88.07 | SF | 1200 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295798 | 57464 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 31 | 1993-07-01 | 4 | 50.35 | 539205.36 | 37600 | 4 | 48.02 | 564469.74 | 1086012.81 | 2018-05-06 | 2021-06-25 14:04 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.Unheated; no water.No standby power generator.No fire alarm system. |  | Jeffrey | Herrick | 2021-06-25 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 88.07 | SF | 1200 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295796 | 57460 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 31 | 1993-07-01 | 4 | 52.48 | 516073.29 | 37600 | 4 | 50.12 | 541728.64 | 1086012.81 | 2018-05-06 | 2021-06-25 13:59 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.Unheated; no water.No standby power generator.No fire alarm system. |  | Jeffrey | Herrick | 2021-06-25 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 88.03 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191563 | 49202 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 26 | 1998-01-01 | 4 | 55.21 | 1632092.15 | 549140 | 4 | 45.75 | 1976857.86 | 3643876.2 | 2018-05-01 | 2024-04-18 19:23 | 2024 | 2029 | 2 | Poor lighting and drainage.Administrative area needs windows and natural lighting.No loading dock or ramp.No additional security measures.No centralized fire alarm system.Constrained truck area; limited Material Handling Equipment capability. |  | Jeffrey | Herrick | 2024-04-18 06:00 | 34 | SMS Complete
6 | 2 | 87.99 | SF | 1200 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295797 | 57462 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 31 | 1993-07-01 | 4 | 48.23 | 562228.83 | 37600 | 4 | 45.94 | 587116.38 | 1086012.81 | 2018-05-06 | 2021-08-16 18:11 | 2021 | 2026 | 2 | Poor lighting and drainage. No Loading dock or ramp. Limited MHE capability. Unheated; no water. No standby power generator. No fire alarm system. |  | Jeffrey | Herrick | 2021-06-25 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 87.21 | SF | 9905 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295543 | 47437 | Operation & Training | Land Operational Facilities | Operational Support Buildings | Security Force Building | 14132 | Ready Bldg | 20 | 2004-02-16 | 3 | 60.9 | 3344161.64 | 596792.73 | 4 | 55.83 | 3777841.28 | 8552843.07 | 2018-06-08 | 2024-08-21 20:46 | 2024 | 2029 | 2 | Reclassified as a Ready Building.Poor drainage and area lighting.No sustainable design or smart meter features.Not handicap accessible.No lobby or backup generator.No loading or supply service area.Cannot have an assembly hall.No Kitchen nor break room No physical fitness area. |  | Jeffrey | Herrick | 2024-04-23 06:00 | 34 | SMS Complete
6 | 2 | 87.21 | SF | 1500 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295543 | 47437 | Supply | Covered Storage | Installation and Organization | Vehicle Storage, Covered | 44263 | Veh Stor Inst | 20 | 2004-02-16 | 4 | 56.25 | 218240.31 | 34807.27 | 4 | 51.82 | 240357.92 | 498835 | 2018-06-08 | 2024-08-21 20:59 | 2024 | 2029 | 2 | Reclassified as Vehicle Storage.; formerly a Ready Building.Poor drainage and area lighting.No sustainable design or smart meter features.Not handicap accessible.No lobby or backup generator.No loading or supply service area.No Kitchen nor break room No physical fitness area.Very constrained truck area; snow removal operations very difficult. |  | Jeffrey | Herrick | 2024-04-23 06:00 | 34 | SMS Complete
6 | 2 | 86.11 | SF | 895 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295817 | 49144 | Supply | Covered Storage | Installation and Organization | Vehicle Storage, Covered | 44263 | Veh Stor Inst | 42 | 1982-07-01 | 4 | 33.33 | 198435.4 | 46500 | 4 | 25.33 | 222254.14 | 297638.22 | 2018-05-13 | 2021-03-30 15:58 | 2021 | 2026 | 2 | Facility does not exist; remove from Real Property records. |  | Jeffrey | Herrick | 2021-03-30 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 85.18 | SF | 8258 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191564 | 57024 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 82 | 1942-01-01 | 3 | 65.3 | 3847312.76 | 938360 | 4 | 58.62 | 4587573.05 | 11087356.65 | 2018-06-05 | 2023-12-05 18:33 | 2024 | 2029 | 2 | Poor lighting and drainage (snow removal).Parking not adjacent to facility.No loading dock.No conference room.Fire alarm system needs additional detectors.No lobby.No emergency power.Lacks storage. |  | Jeffrey | Herrick | 2023-12-04 06:00 | 34 | SMS Complete
6 | 2 | 84.58 | SF | 5310 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295851 | 49142 | Supply | Covered Storage | Depot and Arsenal Covered Stor | Covered Storage Building, Depo | 44110 | Storage Gp Dep | 36 | 1988-01-01 | 4 | 58.45 | 2371230.17 | 482302.44 | 4 | 52.47 | 2712339.71 | 5706931.81 | 2018-05-11 | 2021-07-07 16:34 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.No standby power generator.Roof has leaks identified. |  | MAJ Mark | Kelliher | 2021-07-07 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 84.58 | SF | 530 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295851 | 49142 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 36 | 1988-01-01 | 4 | 57.75 | 300646.2 | 60137.56 | 4 | 51.39 | 345918.41 | 711588.64 | 2018-05-11 | 2021-07-07 16:31 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.No standby power generator. |  | Jeffrey | Herrick | 2021-07-07 06:00 | 34 | SMS Complete
6 | 2 | 82.9 | SF | 256 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1030693 | 57421 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 22 | 2002-07-01 | 4 | 43.54 | 131669.28 | 11500 | 4 | 40.78 | 138111.23 | 233208.08 | 2018-05-06 | 2021-06-30 17:02 | 2021 | 2026 | 2 | A shed.Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.Unheated; no water.No standby power generator. |  | Jeffrey | Herrick | 2021-06-30 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 82.82 | SF | 19676 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191243 | 47430 | Maintenance & Production | Maintenance Facilities | Aircraft Maintenance Facilitie | Aircraft Maintenance Hangar | 21114 | Ac Maint Bay | 66 | 1958-09-01 | 3 | 62.54 | 9714586.09 | 3533710 | 4 | 54.25 | 11865449.07 | 25933225 | 2018-05-28 | 2021-07-13 16:07 | 2021 | 2026 | 2 | Facility is outdated and not sized to adequately house assigned CH-47 aircraft.Poor lighting and drainage.Poor accessibility; not ADA compliant.No security measures. No secure storage; must use adjacent Flight Ops facility.Administrative areas lack comm, SIPR?NIPR and systems furniture.HVAC systems requires major upgrade; HEAT LOSS AND RECOVERY IN WINTER EFFECT OPERATIONS.No lobby area or arctic entry.Lacks storage.Bo Osha certified battery shop.No loading dock nor ramp.No standby emergency power generator |  | Jeffrey | Herrick | 2021-07-13 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 82.59 | SF | 10070 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190964 | 47420 | Operation & Training | Land Operational Facilities | Airfield Operational Buildings | Aviation Operations Building | 14112 | Avn Unit Ops | 33 | 1991-07-01 | 3 | 65.33 | 5085002.63 | 1181150 | 4 | 59.06 | 6004576.86 | 14666866.54 | 2018-06-12 | 2021-07-15 13:27 | 2021 | 2026 | 2 | Facility is used and configured s Aviation Unit Ops, not an Air Passenger Terminal as in Real Property reords.Poor lighting and drainage.Not handicap accessible.No lobby.No Loading dock or ramp.No smart sensors nor meters.No Kitchenette, physical fitness area.No standby power generator (unit is trailer mounted/non-operational), no UPS.No security measures. |  | Jeffrey | Herrick | 2021-07-15 06:00 | 34 | SMS Complete
6 | 2 | 80.83 | SF | 3308 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191210 | 57503 | Operation & Training | Training Facilities | Training Buildings | General Purpose Instruction Bu | 17120 | Gen Inst Bldg | 35 | 1989-07-01 | 4 | 53.25 | 2244258.37 | 573683.59 | 4 | 43.47 | 2713790.3 | 4800552.67 | 2018-06-04 | 2021-07-07 17:24 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.No auditorium or loungeNo standby power generator. |  | Jeffrey | Herrick | 2021-07-07 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 2 | 80.83 | SF | 1800 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191210 | 57503 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 35 | 1989-07-01 | 4 | 58.11 | 1012362.4 | 288806.41 | 4 | 49.09 | 1230252.71 | 2416716.15 | 2018-06-04 | 2021-07-07 17:14 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.No lobby.No standby power generator. |  | Jeffrey | Herrick | 2021-07-07 06:00 | 34 | SMS Complete
6 | 2 | 80.02 | SF | 5122 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295808 | 60606 | Housing & Community | Unaccompanied Personnel Housin | Enlisted Unaccompanied Personn | Enlisted Unaccompanied Personn | 72112 | Warrior In Transition Uh | 50 | 1974-07-01 | 4 | 57.73 | 3153404.56 | 865350 | 4 | 50.66 | 3680614.89 | 7460148 | 2018-05-20 | 2024-08-21 19:43 | 2024 | 2025 | 1 | Not a sustainable design, no smart sensors.Poor drainage and lighting. Not accessible nor ADA compliant.No windows, ceilings or proper flooring in troop barracks area; a modified warehouse.No lobby.Needs an administrative area, better communications and wiFi.Heating system needs updated..No security measures.Does not meet minimum space standards of 90 s.f. nor 149 sf per soldier.Not enough washers/dryers for population capacity and no scrub sinks. |  | Jeffrey | Herrick | 2024-03-05 06:00 | 12, 13, 34 | Barrack, Annual Inspection, SMS Complete
6 | 3 | 77.94 | SF | 42245 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191559 | 47427 | Maintenance & Production | Maintenance Facilities | Aircraft Maintenance Facilitie | Aircraft Maintenance Hangar | 21110 | Ac Maint Hgr | 48 | 1976-01-01 | 4 | 54.39 | 25247027.76 | 8726210 | 4 | 44.78 | 30567316.07 | 55354149.89 | 2018-06-12 | 2021-06-17 13:51 | 2021 | 2026 | 2 | Poor lighting and drainage.Poor accessibility; not ADA compliant.No security measures.Lacks secure storage; uses Flight Ops building across the street.Administrative areas need total restoration.No lobby.Deluge sprinklers are inop at this time.Latrines are under renovation; occupants utilize adjacent facilities.No Loading dock or ramp.No standby power generator. |  | Jeffrey | Herrick | 2021-05-24 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 3 | 77.13 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 969789 | 49208 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 18 | 2006-07-01 | 4 | 53.8 | 1683470.8 | 240250 | 4 | 49.72 | 1832188 | 3643876.2 | 2018-05-02 | 2022-06-28 13:59 | 2022 | 2027 | 2 | Pre-Engineered building; poor insulation, poor drainage and lighting. No plumbing nor latrines.HVAC is inefficient unit heaters.No security systems.No fire panel nor suppression systems.No loading dock nor ramp; very limited MHE capability. |  | Jeffrey | Herrick | 2022-06-28 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 3 | 71.15 | SF | 3393 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295807 | 60820 | Operation & Training | Training Facilities | Training Buildings | General Purpose Instruction Bu | 17120 | Gen Inst Bldg | 50 | 1974-07-01 | 3 | 60.64 | 1938048.71 | 1381362.61 | 4 | 37.05 | 3099827.09 | 4923904.24 | 2018-05-10 | 2023-06-09 18:01 | 2023 | 2028 | 2 | No auditorium, proper lobby or lounge areas.Minimal storage areas. |  | Jeffrey | Herrick | 2023-06-09 06:00 | 34 | SMS Complete
6 | 3 | 71.15 | SF | 2257.5 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295807 | 60820 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 50 | 1974-07-01 | 3 | 62.12 | 779006.98 | 576938.44 | 4 | 43.22 | 1167633.57 | 2056512.63 | 2018-05-10 | 2023-06-09 18:00 | 2023 | 2028 | 2 | Storage Unit of measure is off; closer to 800 sf. and not 3,010. |  | Jeffrey | Herrick | 2023-06-09 06:00 | 34 | SMS Complete
6 | 3 | 71.15 | SF | 5385.5 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295807 | 60820 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 50 | 1974-07-01 | 4 | 59.46 | 2931317.86 | 2028510.54 | 4 | 38.12 | 4474351.54 | 7230680.46 | 2018-05-10 | 2023-06-09 17:59 | 2023 | 2028 | 2 | Poor exterior lighting and drainage.Not handicap accessible.No lobby nor security systems.No secure storageNo kitchenette or break area. |  | Jeffrey | Herrick | 2023-06-09 06:00 | 34 | SMS Complete
6 | 3 | 71.15 | SF | 4515 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295807 | 60820 | Housing & Community | Unaccompanied Personnel Housin | Enlisted Unaccompanied Personn | Student Barracks | 72122 | Trans Uph AST | 50 | 1974-07-01 | 3 | 63.85 | 1538725.79 | 1194128.41 | 4 | 43.37 | 2410468.95 | 4256502.89 | 2018-05-10 | 2024-03-07 22:30 | 2024 | 2025 | 1 | Site has poor lighting and drainage.Facility not entirely compliant with American Disabilities Act.Not all Anti-terrorism assessments have been incorporatedParking is within 33' of facilityNo lobby, emergency power nor security systems.Very constrained laundry area.Does not meet 90 sf per soldier requirementNo energy management system nor smart sensors.No emergency power generator. |  | Jeffrey | Herrick | 2024-03-07 06:00 | 12, 13, 34 | Barrack, Annual Inspection, SMS Complete
6 | 3 | 69.89 | SF | 4661 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191570 | 60802 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 50 | 1974-01-01 | 3 | 63.51 | 2283526.76 | 1609170 | 4 | 43.45 | 3538704.26 | 6257952.21 | 2018-06-11 | 2021-07-07 15:56 | 2021 | 2026 | 2 | Poor exterior lighting and drainage.Not handicap accessible.No hood/duct over kitchen stove.No lobby nor security systems.No secure storage |  | MAJ Mark | Kelliher | 2021-07-07 06:00 | 34 | SMS Complete
6 | 3 | 67.04 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 969790 | 49209 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 16 | 2008-05-01 | 4 | 56.14 | 1598204.1 | 346250 | 4 | 50.12 | 1817637.1 | 3643876.2 | 2018-05-02 | 2021-06-24 17:04 | 2021 | 2026 | 2 | Poor lighting and drainage.No loading dock or ramp.No latrine or admin area.No additional security measures.No centralized fire alarm system.Constrained truck area; limited Material Handling Equipment capability. |  | Jeffrey | Herrick | 2021-06-24 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 3 | 62.91 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295786 | 49210 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 26 | 1998-01-01 | 4 | 52.05 | 1747238.64 | 389690 | 4 | 45.54 | 1984291.59 | 3643876.2 | 2018-05-16 | 2022-06-28 14:11 | 2022 | 2027 | 2 | Poor lighting and drainage.No water/sewer connections.No loading dock or ramp.No additional security measures.No centralized fire alarm system.Constrained truck area; limited Material Handling Equipment capability.Latrine Water Heater needs GFCI outlet.No Nipr/Sipr connectivity nor phone. |  | Jeffrey | Herrick | 2022-06-28 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 3 | 62.03 | SF | 1500 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191203 | 48000 | Operation & Training | Land Operational Facilities | Airfield Operational Buildings | Air Control Tower | 13310 | Flt Cont Tower | 63 | 1961-07-01 | 3 | 71.59 | 2087009.55 | 643150 | 3 | 65.14 | 2561015.07 | 7346038.54 | 2018-06-11 | 2021-08-23 14:20 | 2021 | 2026 | 2 | No sustainable design features; lacks smart sensors and Energy management.Not handicap accessible; no tower elevator.Interior electric cannot handle loads; breakers constantly need reset.Bare minimum (1) latrine fixtures and space.No lobby or arctic entryway; stairwell loses heat.No cooling system; HVAC can barely keep tower windows from fogging and condensation builds.No breakroom; very limited storage; constrained office area. |  | Jeffrey | Herrick | 2021-08-21 06:00 | 34 | SMS Complete
6 | 3 | 61.93 | SF | 5160 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295814 | 57226 | Housing & Community | Unaccompanied Personnel Housin | Enlisted Unaccompanied Personn | Enlisted Unaccompanied Personn | 72112 | Warrior In Transition Uh | 36 | 1988-01-01 | 4 | 57.73 | 3176799.6 | 318270 | 4 | 55.15 | 3370704.07 | 7515494.67 | 2018-05-30 | 2024-08-21 19:36 | 2024 | 2025 | 1 | Not a sustainable design, no smart sensors.Poor drainage and lighting; unpaved.Not accessible nor ADA compliant.No lobby.Needs an administrative area, better communications and wiFi.Heating system is failing; needs replaced.No security measures.Does not meet minimum space standards of 90 s.f.Not enough washers/dryers for population capacity and no scrub sinks.Unpaved and unmarked parking area with no curbs or bollards to protect facility. |  | Jeffrey | Herrick | 2024-03-05 06:00 | 12, 13, 34 | Barrack, Annual Inspection, SMS Complete
6 | 3 | 61.51 | SF | 4625 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191571 | 47432 | Operation & Training | Land Operational Facilities | Operational Support Buildings | Security Force Building | 14132 | Ready Bldg | 64 | 1960-09-01 | 3 | 60.77 | 1566700.81 | 1083590 | 4 | 41.07 | 2353344.17 | 3993629.4 | 2018-06-11 | 2024-08-21 20:08 | 2024 | 2029 | 2 | Reclassified as a Ready facility.Poor drainage and area lighting.No sustainable design or smart meter features.Not handicap accessible.No secure areas or vault.Inadequate latrines; no showers nor lockers.No lobby or backup generator.No loading or supply service area.Cannot have any Ready bays for equipment or maintenance.Does not have a break room No physical fitness area. |  | Jeffrey | Herrick | 2024-04-23 06:00 | 34 | SMS Complete
6 | 4 | 57.54 | SF | 17300 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 619429 | 49040 | Maintenance & Production | Maintenance Facilities | Tank and Automotive Maintenanc | Vehicle Maintenance Shop, Nati | 21407 | Arng Veh Maint | 34 | 1990-01-01 | 3 | 75.9 | 7640370.52 | 5214320 | 3 | 62.78 | 11799206.65 | 31702782.24 | 2018-05-17 | 2024-08-20 14:47 | 2024 | 2029 | 2 | Inadequate drainage and snow removal.No loading dock.No emergency power generator on standby.No secure storage.Overhead doors do not meet 14'x24' Army Standard.Lacks security cameras and controls.No lobby. |  | Jeffrey | Herrick | 2024-08-20 06:00 | 34 | SMS Complete
6 | 4 | 50.79 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295785 | 49206 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 25 | 1999-07-01 | 4 | 56.73 | 1576705.23 | 516950 | 4 | 47.69 | 1906277.77 | 3643876.2 | 2018-05-02 | 2021-06-24 17:10 | 2021 | 2026 | 2 | Poor lighting and drainage.No loading dock or ramp.No additional security measures.N admin area or latrineNo centralized fire alarm system.Constrained truck area; limited Material Handling Equipment capability. |  | Jeffrey | Herrick | 2021-06-24 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 4 | 46.46 | SF | 1440 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 191566 | 57040 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 60 | 1964-01-01 | 3 | 60.48 | 764068.98 | 591190 | 4 | 37.07 | 1216594.84 | 1933372.92 | 2018-05-09 | 2023-12-05 18:33 | 2024 | 2029 | 2 | Facility has been renovated since BUILDER ratings have been input; BUILDER program is dated and facility needs re-inspection for correct Quality ratings and R&M costs.No lobby, small offices, outdated kitchenette.No security and poor standoff. |  | Jeffrey | Herrick | 2023-12-05 06:00 | 34 | SMS Complete
6 | 4 | 42.31 | SF | 1600 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190970 | 60808 | Operation & Training | Training Facilities | Training Buildings | Organizational Classroom | 17119 | Org Classroom | 50 | 1974-07-01 | 4 | 57.29 | 991688.53 | 629245.92 | 4 | 36.37 | 1477417.26 | 2321911.81 | 2018-05-09 | 2021-06-30 13:23 | 2021 | 2026 | 2 | Poor drainage and lighting.Parking has no standoff; undersized and needs resurfaced and striping.No lobby or emergency power.Classrooms lack zonal lighting and Audio-visual capability. |  | Jeffrey | Herrick | 2021-06-28 06:00 | 34 | SMS Complete
6 | 4 | 42.31 | SF | 533 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 190970 | 60808 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 50 | 1974-07-01 | 4 | 56.04 | 212050.16 | 130724.08 | 4 | 37.06 | 303614.29 | 482370.69 | 2018-05-09 | 2021-06-29 12:54 | 2021 | 2026 | 2 | Should be categorized as Administrative.Poor lighting and drainage.Not ADA/Handicap accessible.No Loading dock or ramp.Zero MHE capability. |  | Jeffrey | Herrick | 2021-06-28 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 4 | 30.86 | SF | 336 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295815 | 57427 | Housing & Community | Unaccompanied Personnel Housin | Officer Unaccompanied Personne | Officer UPH, Transient | 72412 | Training Collective Uh, Senior | 82 | 1942-01-01 | 4 | 55.69 | 143330.43 | 171600 | 4 | 18.37 | 264063.56 | 323471.98 | 2018-05-06 | 2023-12-05 22:46 | 2024 | 2025 | 1 | BUILDER Quality rating is incorrect, needs overwritten and re-inspected.Facility has black mold and is deemed uninhabitable currently. Roof leaks and trusses/rafters have failed structurally.Poor lighting and drainageNo parking standoff.No lobby or lounge area.No security measures.Not handicap accessible.No smart sensors nor meters.Roof and siding need total restoration project; planned for demolition, pursuing FY24 funding.. |  | Jeffrey | Herrick | 2023-11-28 06:00 | 12, 13, 34 | Barrack, Annual Inspection, SMS Complete
6 | 4 | 24.13 | SF | 2133 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295801 | 60806 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 50 | 1974-07-01 | 4 | 58.33 | 804392.59 | 425060 | 4 | 42.64 | 1107280.71 | 1930387.78 | 2018-05-10 | 2021-06-29 12:47 | 2021 | 2026 | 2 | Should be categorized as Administrative.Poor lighting and drainage.Not ADA/Handicap accessible.No Loading dock or ramp.Zero MHE capability.No security measures. |  | Jeffrey | Herrick | 2021-06-28 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 4 | 21.82 | SF | 22880 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295538 | 49140 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 45 | 1979-01-01 | 3 | 70.97 | 8542355.09 | 5742922.15 | 4 | 55.56 | 13078208.78 | 29425956.23 | 2018-05-11 | 2023-07-12 13:47 | 2023 | 2028 | 2 | Former USPFO; INF Battalion armory now.No smart network nor sustainable design.Is not ADA accessible.Needs a lobby, an Assembly hall, commercial kitchen. |  | Jeffrey | Herrick | 2023-07-10 06:00 | 34 | SMS Complete
6 | 4 | 21.82 | SF | 1647 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295538 | 49140 | Administrative | Administrative Buildings | Administrative Buildings | General Administrative Buildin | 61050 | Admin Gen Purp | 45 | 1979-01-01 | 3 | 62.34 | 832773.8 | 431567.85 | 4 | 47.23 | 1166946.97 | 2211295.28 | 2018-05-11 | 2021-07-07 15:35 | 2021 | 2026 | 2 | Primary usage is an Admin facility (USPFO).Inadequate lighting and drainage.Roof leaks at warehouse.No loading dock nor lobby.No dedicated uninterrupted power in warehouse/admin area. |  | Jeffrey | Herrick | 2021-07-07 06:00 | 34 | SMS Complete
6 | 4 | 16.8 | SF | 1250 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 295805 | 57426 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 35 | 1989-01-01 | 4 | 57.78 | 480763.92 | 273170 | 4 | 42.32 | 656782.75 | 1138711.31 | 2018-05-09 | 2021-06-30 17:25 | 2021 | 2026 | 2 | Poor lighting and drainage.No Loading dock or ramp.Limited MHE capability.No standby power generator. |  | Jeffrey | Herrick | 2021-06-30 06:00 | 25, 34 | Incomplete Rating, SMS Complete
6 | 4 | 13.18 | SF | 4000 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1152566 | 57410 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44224 | Org Str Bldg | 11 | 2012-11-13 | 4 | 52.24 | 1740315.27 | 904700 | 4 | 37.11 | 2291693.71 | 3643876.2 | 2018-05-09 | 2024-04-22 22:38 | 2024 | 2029 | 2 | Engineer unit storage.Poor lighting and drainage.No lobby and no windowsNo Loading dock or ramp.Limited MHE capability.No standby power generator.No security systems. |  | Jeffrey | Herrick | 2024-04-22 06:00 | 34 | SMS Complete
6 | 4 | 7.42 | SF | 1900 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1061808 | 60810 | Operation & Training | Training Facilities | Training Buildings | Organizational Classroom | 17119 | Org Classroom | 14 | 2010-09-07 | 3 | 62.5 | 1033976.36 | 1047537.02 | 4 | 32.33 | 1865951.25 | 2757270.28 | 2018-05-09 | 2021-06-30 13:29 | 2021 | 2026 | 2 | Poor lighting, drainage.No security measures and no standoff.no proper admin area or storage.No Lobby.Not ADA compliant.No service or loading area.No emergency power. |  | Jeffrey | Herrick | 2021-06-28 06:00 | 34 | SMS Complete
6 | 4 | 7.42 | SF | 1100 | 020NG | Alaska National Guard | 5043 | HJZH0001 | FORT RICHARDSON SITE 1 | Fort Richardson | 1061808 | 60810 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 14 | 2010-09-07 | 4 | 55.05 | 447482.53 | 378212.98 | 4 | 28.63 | 710457.11 | 995511.75 | 2018-05-09 | 2021-06-29 12:59 | 2021 | 2026 | 2 | Poor lighting and drainage.Not ADA/Handicap accessible.No Loading dock or ramp.Zero MHE capability.No security measures. |  | Jeffrey | Herrick | 2021-06-28 06:00 | 25, 34 | Incomplete Rating, SMS Complete
7 | 1 | 99.55 | SF | 1024 | 020NG | Alaska National Guard | 6482 | 02C01 | Kotzebue Armory | Kotzebue | 562599 | 2 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 74 | 1950-01-01 | 4 | 49.71 | 693609.38 | 6070 | 4 | 49.42 | 697669.39 | 1379219.28 | 2019-08-27 | 2023-01-05 13:14 | 2023 | 2028 | 2 | Square footage in FISP is incorrect; should be 120 s.f. not 1200.Small, unheated wooden shed on wood pilings; should be re-classified in real property records.Unpaved, poorly lit, constrained truck area..No loading dock nor ramp.No fire detection nor extinguishers.Cannot support MHE. |  | Jeffrey | Herrick | 2022-12-21 06:00 | 34 | SMS Complete
7 | 1 | 95.24 | SF | 2880 | 020NG | Alaska National Guard | 6508 | 2611 | Utqiagvik Armory | UTQIAGVIK | 1361924 | 2 | Housing & Community | Unaccompanied Personnel Housin | Enlisted Unaccompanied Personn | Annual Training/Mobilization B | 72114 | Tt Enl Barracks | 7 | 2016-10-12 | 3 | 63.49 | 1574754.13 | 188500 | 3 | 60.43 | 1706532.05 | 4313213.18 | 2019-05-29 | 2024-04-09 15:06 | 2024 | 2025 | 1 | Alarm system is in alarm and needs serviced.Carbon Monoxide circuit switch has trouble light.No remote sensors nor smart meters.Poor lighting, drainage.Half the washers are broken need work order repairs.No security measures z; door lock system in-op and no standoff.Does not meet 72sf minimum Army space standard.No Lobby.Not ADA compliant.Lacks adequate parking.; unpaved.No emergency power generator |  | Jeffrey | Herrick | 2024-03-29 06:00 | 12, 13, 34 | Barrack, Annual Inspection, SMS Complete
7 | 1 | 93.71 | SF | 17407 | 020NG | Alaska National Guard | 6502 | 02C50 | Nome AAOF | Nome | 562601 | 1 | Maintenance & Production | Maintenance Facilities | Aircraft Maintenance Facilitie | Aircraft Maintenance Hangar | 21114 | Ac Maint Bay | 35 | 1989-01-01 | 4 | 58.08 | 14313458.27 | 2038660 | 4 | 54.66 | 15479856.29 | 34144700.08 | 2022-04-27 | 2021-07-14 11:08 | 2021 | 2026 | 2 | Previously categorized as a Maintenance Hangar or a AAOF (now a Bay); facility cannot perform most maintenance functions and is more operational.. Poor drainage & lighting and unpaved. Roof leaks on east side exterior wall. Siding above hangar door needs replacement and structural reinforcement to handle wind loads. No loading ramp. Minimal secure storage. Crane and hoist are under-sized and cannot reach 66% of the floor maintenance areas. |  | Jeffrey | Herrick | 2020-10-02 06:00 | 25, 34 | Incomplete Rating, SMS Complete
7 | 1 | 92.28 | SF | 14817 | 020NG | Alaska National Guard | 6503 | 02C55 | Nome Armory | Nome | 562602 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 62 | 1962-01-01 | 3 | 71.83 | 7989164.27 | 2029400 | 3 | 66.14 | 9602896.36 | 28360540.55 | 2022-04-27 | 2020-09-16 21:54 | 2020 | 2025 | 2 | Roof is leaking severely; needs a BUILDER update inspection to capture Q ratings and Restoration costs.Facility primarily used by Alaska State Troopers.Poor lighting and drainage.Roof trusses broken during previous winter snow load and wind loading; 15% of roof needs replaced.No emergency power. Lacks secure storage space.No kitchen.Arms room alarms disconnected. |  | Jeffrey | Herrick | 2020-09-15 06:00 | 25, 34 | Incomplete Rating, SMS Complete
7 | 1 | 90.69 | SF | 2109 | 020NG | Alaska National Guard | 6502 | 02C50 | Nome AAOF | Nome | 556186 | 3 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 21 | 2003-01-01 | 4 | 54.39 | 1297568.6 | 264915.46 | 4 | 47.88 | 1482865.95 | 2844921.28 |  | 2024-08-19 14:41 | 2024 | 2029 | 2 | Duplicate entry of FAC 0003; should be revised and removed from Real Property records |  | Jeffrey | Herrick | 2024-06-12 06:00
7 | 2 | 87.31 | SF | 240 | 020NG | Alaska National Guard | 6502 | 02C50 | Nome AAOF | Nome | 567843 | 2 | Operation & Training | Land Operational Facilities | Operational Support Buildings | Miscellaneous Operations Suppo | 14165 | Fuel/Pol Bldg | 35 | 1989-01-01 | 4 | 50 | 241604.45 | 61332.65 | 4 | 41.39 | 283206.91 | 483208.89 |  | 2024-06-12 23:26 | 2024 | 2029 | 2 | Facility has been decommissioned for several years; non-operational, has no fuel. Dispensing equipment disconnected and removed |  | Jeffrey | Herrick | 2024-06-12 06:00
7 | 2 | 86.47 | SF | 3600 | 020NG | Alaska National Guard | 6508 | 2611 | Utqiagvik Armory | UTQIAGVIK | 561171 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 60 | 1964-01-01 | 4 | 49.51 | 3653014.48 | 906750 | 4 | 41.07 | 4263413.19 | 7235124.74 | 2019-05-28 | 2022-10-31 11:59 | 2023 | 2026 | 2 | Site has poor drainage, poor lighting, no room for expansionUnpaved parkingInaccessible for handicapped.No lobby.No emergency power generator.No fire suppression or central fire panel.Security system has camera only for front doors.No loading dock.No arms vault.Kitchen is residential grade; no fire suppression.No designated classroom or training area.No physical fitness equipment or area.Does not meet Army standard 5,400 square feet for assembly hall. |  | Jeffrey | Herrick | 2022-10-27 06:00 | 10, 34 | Historic, SMS Complete
7 | 2 | 86.06 | SF | 2849 | 020NG | Alaska National Guard | 6503 | 02C55 | Nome Armory | Nome | 562606 | 2 | Maintenance & Production | Maintenance Facilities | Tank and Automotive Maintenanc | Vehicle Maintenance Shop, Nati | 21407 | Arng Veh Maint | 64 | 1960-01-01 | 4 | 54.85 | 3508174.09 | 1061850 | 4 | 45.84 | 4208200.3 | 7770042.29 | 2022-04-27 | 2024-06-12 23:30 | 2024 | 2029 | 2 | Location Comment: Poor location / not enough property for parking vehicles, poor truck area.Unpaved, not enough space for equipment or material.Poor lighting, limited access.No safe loading dock (they utilize exterior stair landings next door).No emergency power / utility power unstable.No sprinkler system / no fire panel.No SIPR/NIPR access.No security measures.Exterior door frames failing due to seasonal movement and weathering.No showers or lockers in latrine. |  | Jeffrey | Herrick | 2024-06-12 06:00 | 34 | SMS Complete
7 | 2 | 83.6 | SF | 800 | 020NG | Alaska National Guard | 6503 | 02C55 | Nome Armory | Nome | 562608 | 3 | Maintenance & Production | Maintenance Facilities | Installation Repair and Operat | Facility Engineer Maintenance | 21910 | Eng/Housing Mnt | 62 | 1962-01-01 | 4 | 47.56 | 743929.9 | 230579.13 | 4 | 35.09 | 920878.44 | 1418630.63 | 2022-04-28 | 2024-06-12 23:31 | 2024 | 2029 | 2 | Location Comment: Building sits on good ground / good location, but poor drainage.Parking lot unpaved, undersized, poorly lit.No loading dock (they utilize exterior stair landings).Exterior stairs and landings have no rails.No emergency or standby power.No fire panel or pull stations.No SIPR/NIPR access.Not functional for assembly fabrication or heavy maintenance operations.Need overhead coiling entrance doorFoundation has severe frost upheaval. |  | Jeffrey | Herrick | 2024-06-12 06:00 | 34 | SMS Complete
7 | 2 | 83.6 | SF | 1600 | 020NG | Alaska National Guard | 6503 | 02C55 | Nome Armory | Nome | 562608 | 3 | Supply | Covered Storage | Installation and Organization | Covered Storage Building, Inst | 44220 | Storage Gp Inst | 62 | 1962-01-01 | 4 | 43.78 | 1211557.93 | 350270.87 | 4 | 33.35 | 1436406.46 | 2155030.12 | 2022-04-28 | 2023-05-22 11:47 | 2023 | 2028 | 2 | Site is poorly lit, bad drainage.Unpaved lot.No loading ramp.There is not enough parking for the equipment.No fire panel or pull station.Cannot support MHE or all storage operations.No SIPR or NIPR connectivity.Inspection done with Steve Smith |  | Jeffrey | Herrick | 2023-05-18 06:00 | 34 | SMS Complete
7 | 2 | 82.66 | SF | 1980 | 020NG | Alaska National Guard | 6502 | 02C50 | Nome AAOF | Nome | 1180031 | 5 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 10 | 2014-01-01 | 4 | 56.06 | 1173596.8 | 463118.93 | 4 | 43.79 | 1501421.39 | 2670907.6 |  | 2024-06-12 23:28 | 2024 | 2029 | 2 | Roof and partial siding protecting 2 decommissioned Jet-A fuel tanks.Allows precipitation, snow and sun onto tank surfaces.Lacks security measures. |  | Jeffrey | Herrick | 2024-06-12 06:00
7 | 3 | 61.62 | SF | 31512 | 020NG | Alaska National Guard | 6482 | 02C01 | Kotzebue Armory | Kotzebue | 568514 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 37 | 1987-01-01 | 3 | 60.57 | 23782470.58 | 13568050 | 4 | 44.17 | 33675970.52 | 60315674.82 | 2019-06-27 | 2023-01-05 13:12 | 2023 | 2028 | 2 | Facility is now Joint-use with Alaska Court System & Alaska State Troopers; they utilize majority of classroom and admin space.No room for expansion; parking areas are unpaved, no sidewalks, poorly lit. Poor site drainage; building sits below surrounding grade.Kitchen has been decommissioned and changed into a holding cell area for the Court.Arms room not utilized and alarms offAssembly Hall does not meet minimum space requirement of 5400sf since admin space walls have been added.No emergency power generator.Indoor firing range lead abatement complete. |  | Jeffrey | Herrick | 2022-12-21 06:00 | 34 | SMS Complete
8 | 1 | 95.14 | SF | 23286 | 020NG | Alaska National Guard | 193281 | 2292 | BETHEL ARMORY | Bethel | 1125547 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 12 | 2011-10-20 | 3 | 64.69 | 15737901.9 | 2006830 | 3 | 61.3 | 17247588.31 | 44570665.26 | 2022-04-23 | 2023-02-21 17:09 | 2023 | 2028 | 2 | Roof has started to leak over drill floor; BUILDER data needs updated as faculty ages the Q1 rating is inaccurate.Site has poor PR visibility & location with limited expansion.Poor drainage and lighting.Not accessible to handicapped.No loading dock nor ramp.Arms room is outside 75' away in secure ARMAG vault but operations hindered by weather and environmental conditions.Administrative area not sized for Battalion training requirement minimums, currently meets company HQ.Only security measures are door locks.Assembly hall is 80% of 5,400 sq ft standard.Water & sewage must be trucked in/out of undersized storage tanks; frequently runs out during operations. Unit supply & storage undersized.Kitchen is not fully functional as commercial grade.Vehicle Maintenance bay used as administrative and facility material storage. |  | Jeffrey | Herrick | 2023-02-21 06:00 | 34 | SMS Complete
8 | 1 | 93.78 | SF | 1500 | 020NG | Alaska National Guard | 6510 | 2621 | Quinhagak Armory | Quinhagak | 558030 | 4 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 19 | 2005-09-28 | 4 | 53.02 | 1348833.97 | 165520 | 4 | 49.04 | 1463042.48 | 2871081.25 | 2019-05-28 | 2020-07-07 17:41 | 2020 | 2025 | 2 | Remote Alaska Location; due to COVID-19 restrictions placed by the local tribal council, access to Quinahagak has been denied and location inspection performed by IDT detachment teaminspection performed during annual State maintenance visit. Building sits on a partial gravel pad but is not sloped well and does not drain.Poorly lit, unpaved, no standoff and no security systems.No loading dock.No running water nor sewerage systems; composting toilet.Electrical provided by others with weekly power interruptions due to utility doing generator maintenance.No security system / door locks and deadbolts.Fire protection is hand held extinguishers and local smoke detectors.Combined with adjacent facilities, there is adequate storage for equipment & administrative spaceDoes notmeet 5400 square foot assembly hall standard. |  | Garis | Kinegak | 2020-07-07 06:00 | 25, 34 | Incomplete Rating, SMS Complete
8 | 1 | 92 | SF | 1560 | 020NG | Alaska National Guard | 6464 | 2521 | Ng Hooper Bay Armory | Hooper Bay | 561554 | 3 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 32 | 1992-01-01 | 4 | 57.68 | 1211821.91 | 212250 | 4 | 52.39 | 1363304.36 | 2863473.33 | 2019-05-08 | 2024-08-16 15:53 | 2024 | 2029 | 2 | Category Code: should be a Storage FacilityNo roads, walkways, boardwalks. Unpaved lot.Doors are worn but functional. leak air only.Foundation is settling unevenly into permafrost/swamp.No loading dock.No running water nor sewer; composting toilet.Electrical: Provided by others with weekly power outages to perform generator maint, no standby power. Fire protection is hand held fire extinguishers and local smoke alarms.Combined with adjacent facilities, admin, storage and classroom size is adequate.Assembly hall does not meet army size standards.Windows, doors and interior were vandalized; requires extensive restoration; ECD in FY24 |  | Jay | Friesen | 2024-07-31 06:00 | 34 | SMS Complete
8 | 3 | 78.84 | SF | 1368 | 020NG | Alaska National Guard | 6510 | 2621 | Quinhagak Armory | Quinhagak | 561172 | 2 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 40 | 1984-01-01 | 4 | 46.28 | 1406618.5 | 513370 | 4 | 33.37 | 1744655.3 | 2618426.1 | 2019-05-28 | 2024-08-20 14:34 | 2024 | 2029 | 2 | Facility was vandalized and has not been repaired.Building sits on a gravel pad but is not sloped well and does not drain/ fair location.No lobby / no walkways / dirt road / no running water.No kitchen, fitness area or latrineHeat is disconnected and tank is closedNo paved roads / no sidewalk / roads are dirt and poor lighting. Unpaved lot; parking for ATV onlyNo loading dock.Toyo Fuel heater damaged; needs replacedWindows broken.Doors leak air and water.Floor tiles coming unglued and subfloor is deteriorated; tripping hazard.No running water / composting toilet.Electrical provided by others with weekly power interruptions due to utility doing generator maintenance.No security system / door locks and deadbolts.Inadequate storage space, admin and classroom areas.Inspection performed by Environmental Compliance Team.BUILDER BRD files need updated and rated down to Red. |  | Jeffrey | Herrick | 2024-06-18 06:00 | 34 | SMS Complete
8 | 3 | 78.46 | SF | 1200 | 020NG | Alaska National Guard | 4015 | 02A65 | Bethel AAOF | Bethel | 244212 | 3 | Operation & Training | Land Operational Facilities | Ground Operational Facilities | Overhead Cover | 14179 | Overhead Protec | 25 | 1999-09-20 | 4 | 59.09 | 662223.21 | 348687.95 | 4 | 43.5 | 914539.25 | 1618731.88 |  | 2024-08-18 22:45 | 2024 | 2029 | 2 | Overhead protection for decommissioned tanks and fuel facility; sides allow snow/rain to engulf area and facilitate metal corrosion. Faciity has 12' STANDING WATER; THEREFORE, DOES NOT LEAK. |  | Jeffrey | Herrick | 2024-05-23 06:00
8 | 3 | 74.53 | SF | 1368 | 020NG | Alaska National Guard | 6464 | 2521 | Ng Hooper Bay Armory | Hooper Bay | 561553 | 2 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 40 | 1984-01-01 | 4 | 51.34 | 1221874.91 | 592570 | 4 | 35.25 | 1625909.73 | 2511045.85 | 2019-05-08 | 2023-06-13 11:09 | 2023 | 2028 | 2 | Red Rating Explanation: Alaska bush Armory A2 / no running water / no sewer / no roads or walkways.Sites & grounds / no roads, walkways, boardwalks.Unpaved lot.Doors are worn but functional.No loading dock.No running water nor sewer; composting toilet.No working heat; fuel oil stove not connected to fuel tank.Corridors are breezeways attaching other building.Electrical: Provided by others with weekly power outages to perform generator maint.Fire protection is hand held fire extinguishers and local smoke alarms.Arms room has no intrusion detection just a deadbolt & door lock with a safe inside for arms.Does not meet minimum space requirements for admin areas, classroom or assembly areas.No kitchen; no fitness area; no standby power generator |  | Jay | Friesen | 2023-06-08 06:00 | 34 | SMS Complete
8 | 3 | 73.84 | SF | 1200 | 020NG | Alaska National Guard | 6464 | 2521 | Ng Hooper Bay Armory | Hooper Bay | 569680 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 64 | 1960-01-01 | 4 | 42.03 | 1340733.28 | 560600 | 4 | 26.51 | 1699659.03 | 2312805.38 | 2019-05-08 | 2023-06-13 11:07 | 2023 | 2026 | 2 | Location Comment: Hooper Bay bush Alaska.Facility is on Divestiture list to be turned over to Village.Site and grounds are dirt roads and walkways, but on high ground.Unpaved, unlit lot.Old corrugated galvanized siding/ no paint remains.No loading dock nor ramp.Corridors are breezeways connecting cold storage building to other 2 bldgs.Building kept cold, but heater is intact, needs maintenanceElectrical service by others / power interrupts weekly for generator maint. (Village power maint).Fire protection is only handhold fire ext with smoke alarms / battery operated (local alarm).Inspection performed by Department of Military Affairs project managers. |  | Jay | Friesen | 2023-06-08 06:00 | 10, 34 | Historic, SMS Complete
8 | 3 | 70.79 | SF | 1200 | 020NG | Alaska National Guard | 6510 | 2621 | Quinhagak Armory | Quinhagak | 569038 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 64 | 1960-01-01 | 4 | 42.65 | 1317252.08 | 621700 | 4 | 25.25 | 1716899.13 | 2296865 | 2019-05-22 | 2021-08-11 17:27 | 2021 | 2026 | 2 | Inspection done by Guardsman Otto Hunter.Building sits on a gravel pad but is not sloped well and does not drain/ good location.Red Rating Explanation: Alaska bush armory / no lobby / no walkways / dirt road / no running water.No paved roads / no sidewalk / roads are dirt and poor lighting. Unpaved lot; parking for ATV onlyWalls deteriorated.Windows are fogged up / hard to see out of them / some missing or broken into.Doors show severe signs of weathering; leak air. Storage door has fallen off hinges.Foundation settling on permafrostNo loading dock.No running water / composting toilet.Electrical provided by others with weekly power interruptions due to utility doing generator maintenance.Heat disconnected.No security system / door locks and deadbolts.Fire protection is hand held extinguishers and local smoke detectors / no fire station.Inadequate storage, classroom and admin space. |  | Garis | Kinegak | 2021-04-19 06:00 | 34 | SMS Complete
8 | 3 | 67.69 | SF | 23396 | 020NG | Alaska National Guard | 4015 | 02A65 | Bethel AAOF | Bethel | 244206 | 2 | Maintenance & Production | Maintenance Facilities | Aircraft Maintenance Facilitie | Aircraft Maintenance Hangar | 21114 | Ac Maint Bay | 25 | 1999-01-01 | 4 | 55.06 | 20624054.79 | 14077900 | 4 | 38.23 | 28347464.01 | 45892422.77 | 2022-04-24 | 2024-07-02 15:27 | 2024 | 2029 | 2 | Fire suppression system accidently discharged; spill of 300 gallons of Poly Fluorinated Alkyd Substances (PFAS); system is inoperable until guidance from NGB of how to proceed with system.Roof membrane is starting to have multiple leaks in Ops/Admin area.Poor accessibility; not ADA compliant.Poor drainage and lighting. No smart meters or timed zoned lighting; not a sustainable design..Lacks security measures and standby power generator.No secure storage.No loading dock/ramp and no storage for dunnage or pallets.No lobby or arctic entryway.Hangar floor peeling; needs re-finished.Incomplete security measures. |  | Jeffrey | Herrick | 2024-05-22 06:00 | 34 | SMS Complete
8 | 4 | 38.16 | SF | 1200 | 020NG | Alaska National Guard | 6474 | 2541 | Ng Kipnuk Armory | Kipnuk | 565535 | 1 | Operation & Training | Training Facilities | Training Buildings | Reserve Training Facility | 17180 | Arng Armory | 64 | 1960-07-06 | 4 | 45.67 | 1310281.09 | 1381880 | 4 | 8.1 | 2216480.26 | 2411708.25 | 2019-05-30 | 2024-08-20 14:40 | 2024 | 2027 | 2 | Location Comment: Sits in a swamp.Grounds swampy; unpaved, unlit.Foundation settling due to permafrostNo parking in the summer months due to standing swamp water.No lobby.Windows need replaced.Composting toilet / no running water.No backup generator / village power unreliable.No fire panel or pull stations.Learning center & Assembly hall do not meet minimum space requirementsNo storage shelving.Inspection performed by Environmental Compliance Team.BUILDER BRD files need updated and rated down to Red. |  | Garis | Kinegak | 2023-10-02 06:00 | 10, 34 | Historic, SMS Complete